## ModbusMap
# ================ Modbus Map =======================
# Date / Time : 01.01.2000 01:01:53
# System-Name : Name of the Unit
# System-Location: Location of the Unit
# System-Contact : Contact Person
# Serial-Number : 10001012
# MAC-Address : 10:CE:A9:A5:6D:BD
# IPv4-Address : 192.168.0.3
# IPv6-Address : n/a
# IPv6-Address : n/a
# IPv6-Address : n/a
# IPv6-Address : fe80::12ce:a9ff:fea5:6dbd/64
# ===================================================
#
Type | Access | Unit | PosInt | PosHex | Size | Label | Description
Coil | ReadWrite | 0 | 0 | 0x0000 | 1 | SetBeeper(0=off/1=on)
Coil | ReadWrite | 0 | 1 | 0x0001 | 1 | QuitRelay(0=disable/1=enable)
Coil | ReadWrite | 0 | 2 | 0x0002 | 1 | UnitMsgRelay(0=disable/1=enable)
Coil | ReadWrite | 0 | 3 | 0x0003 | 1 | QuitUnit(0=no/1=yes)
DiscreteInput | ReadOnly | 0 | 0 | 0x0000 | 1 | global access | 0
DiscreteInput | ReadOnly | 0 | 1 | 0x0001 | 1 | client access | 0
HoldingRegister | ReadWrite | 0 | 0 | 0x0000 | 1 | cmcIIILogicRelay
HoldingRegister | ReadWrite | 0 | 1 | 0x0001 | 1 | cmcIIIFunctionRelay
InputRegister | ReadOnly | 0 | 0 | 0x0000 | 11 | system identification | RITTAL CMCIII
InputRegister | ReadOnly | 0 | 11 | 0x000B | 3 | mac address | 10:CE:A9:A5:6D:BD
InputRegister | ReadOnly | 0 | 14 | 0x000E | 6 | available units
InputRegister | ReadOnly | 0 | 20 | 0x0014 | 1 | cmcIIIUnitType | 8
InputRegister | ReadOnly | 0 | 21 | 0x0015 | 2 | cmcIIIUnitSerial | 0x10001012
InputRegister | ReadOnly | 0 | 23 | 0x0017 | 2 | cmcIIIUnitUpTime
InputRegister | ReadOnly | 0 | 25 | 0x0019 | 1 | cmcIIIUnitStatus
InputRegister | ReadOnly | 0 | 26 | 0x001A | 1 | cmcIIIOverallDevStatus
InputRegister | ReadOnly | 0 | 27 | 0x001B | 1 | cmcIIIOverallMsgStatus
InputRegister | ReadOnly | 0 | 28 | 0x001C | 1 | cmcIIINumberOfDevs
InputRegister | ReadOnly | 0 | 29 | 0x001D | 2 | cmcIIILastChangeDevs
InputRegister | ReadOnly | 0 | 31 | 0x001F | 1 | cmcIIINumberOfVars
InputRegister | ReadOnly | 0 | 32 | 0x0020 | 2 | cmcIIILastChangeVars
InputRegister | ReadOnly | 0 | 34 | 0x0022 | 1 | cmcIIINumberOfMsgs
InputRegister | ReadOnly | 0 | 35 | 0x0023 | 1 | cmcIIIUnitCurrentSource
InputRegister | ReadOnly | 0 | 36 | 0x0024 | 1 | cmcIIICan0CurrentConsumption
InputRegister | ReadOnly | 0 | 37 | 0x0025 | 1 | cmcIIICan1CurrentConsumption
InputRegister | ReadOnly | 0 | 38 | 0x0026 | 1 | cmcIIIUnitMode
DeviceIdentification | ReadOnly | 0 | 0 | 0x00 | 10 | vendor name | Rittal GmbH & Co. KG
DeviceIdentification | ReadOnly | 0 | 1 | 0x01 | 2 | product code | CMC
DeviceIdentification | ReadOnly | 0 | 2 | 0x02 | 2 | major.minor version | 1.04
DeviceIdentification | ReadOnly | 0 | 3 | 0x03 | 11 | vendor URL | http://www.rittal.com
DeviceIdentification | ReadOnly | 0 | 4 | 0x04 | 32 | product name | CMCIII
DeviceIdentification | ReadOnly | 0 | 5 | 0x05 | 32 | model name | Computer Multi Control III
DeviceIdentification | ReadOnly | 0 | 6 | 0x06 | 4 | application name | cmc3mbd
DeviceIdentification | ReadOnly | 0 | 128 | 0x80 | 9 | mac address | 10:CE:A9:A5:6D:BD
DeviceIdentification | ReadOnly | 0 | 129 | 0x81 | 5 | cmcIIIDevSerial | 0x10001012
DeviceIdentification | ReadOnly | 0 | 130 | 0x82 | 32 | cmcIIIDevName | IoT Interface
DeviceIdentification | ReadOnly | 0 | 131 | 0x83 | 16 | cmcIIIDevArtNr | 3124.3
DeviceIdentification | ReadOnly | 0 | 132 | 0x84 | 16 | cmcIIIDevFW | V6.15.70
DeviceIdentification | ReadOnly | 0 | 133 | 0x85 | 16 | cmcIIIDevHW | V1.0.2
DeviceIdentification | ReadOnly | 0 | 134 | 0x86 | 16 | cmcIIIUnitOSRev | 4.14.78-ge7405910ca
DeviceIdentification | ReadOnly | 0 | 135 | 0x87 | 4 | cmcIIIDevProductWeek | 12/2019
DeviceIdentification | ReadOnly | 0 | 136 | 0x88 | 32 | sysName | Name of the Unit
DeviceIdentification | ReadOnly | 0 | 137 | 0x89 | 32 | sysLocation | Location of the Unit
DeviceIdentification | ReadOnly | 0 | 138 | 0x8A | 32 | sysContact | Contact Person
HoldingRegister | ReadWrite | 1 | 0 | 0x0000 | 2 | cmcIIIVarValueInt | Temperature.Offset 2
HoldingRegister | ReadWrite | 1 | 2 | 0x0002 | 2 | cmcIIIVarValueInt | Temperature.SetPtHighAlarm 3
HoldingRegister | ReadWrite | 1 | 4 | 0x0004 | 2 | cmcIIIVarValueInt | Temperature.SetPtHighWarning 4
HoldingRegister | ReadWrite | 1 | 6 | 0x0006 | 2 | cmcIIIVarValueInt | Temperature.SetPtLowWarning 5
HoldingRegister | ReadWrite | 1 | 8 | 0x0008 | 2 | cmcIIIVarValueInt | Temperature.SetPtLowAlarm 6
HoldingRegister | ReadWrite | 1 | 10 | 0x000A | 2 | cmcIIIVarValueInt | Temperature.Hysteresis 7
HoldingRegister | ReadWrite | 1 | 12 | 0x000C | 2 | cmcIIIVarValueInt | Temperature.Category 9
HoldingRegister | ReadWrite | 1 | 14 | 0x000E | 2 | cmcIIIVarValueInt | System.CAN1 Current.SetPtHighAlarm 12
HoldingRegister | ReadWrite | 1 | 16 | 0x0010 | 2 | cmcIIIVarValueInt | System.CAN1 Current.SetPtHighWarning 13
HoldingRegister | ReadWrite | 1 | 18 | 0x0012 | 2 | cmcIIIVarValueInt | System.CAN1 Current.Hysteresis 14
HoldingRegister | ReadWrite | 1 | 20 | 0x0014 | 2 | cmcIIIVarValueInt | System.CAN1 Current.Category 16
HoldingRegister | ReadWrite | 1 | 22 | 0x0016 | 2 | cmcIIIVarValueInt | System.CAN2 Current.SetPtHighAlarm 19
HoldingRegister | ReadWrite | 1 | 24 | 0x0018 | 2 | cmcIIIVarValueInt | System.CAN2 Current.SetPtHighWarning 20
HoldingRegister | ReadWrite | 1 | 26 | 0x001A | 2 | cmcIIIVarValueInt | System.CAN2 Current.Hysteresis 21
HoldingRegister | ReadWrite | 1 | 28 | 0x001C | 2 | cmcIIIVarValueInt | System.CAN2 Current.Category 23
HoldingRegister | ReadWrite | 1 | 30 | 0x001E | 2 | cmcIIIVarValueInt | System.CAN Supply.Category 26
HoldingRegister | ReadWrite | 1 | 32 | 0x0020 | 2 | cmcIIIVarValueInt | System.Supply 24V.Category 29
HoldingRegister | ReadWrite | 1 | 34 | 0x0022 | 2 | cmcIIIVarValueInt | System.Supply Cooling 1.Category 32
HoldingRegister | ReadWrite | 1 | 36 | 0x0024 | 2 | cmcIIIVarValueInt | Memory.USB-Stick.Command 36
HoldingRegister | ReadWrite | 1 | 38 | 0x0026 | 2 | cmcIIIVarValueInt | Memory.USB-Stick.Category 38
HoldingRegister | ReadWrite | 1 | 40 | 0x0028 | 2 | cmcIIIVarValueInt | Memory.SD-Card.Command 42
HoldingRegister | ReadWrite | 1 | 42 | 0x002A | 2 | cmcIIIVarValueInt | Memory.SD-Card.Category 44
HoldingRegister | ReadWrite | 1 | 44 | 0x002C | 2 | cmcIIIVarValueInt | Webcam.Command 46
HoldingRegister | ReadWrite | 1 | 46 | 0x002E | 2 | cmcIIIVarValueInt | Webcam.Category 48
InputRegister | ReadOnly | 1 | 0 | 0x0000 | 1 | cmcIIIDevIndex | 1
InputRegister | ReadOnly | 1 | 1 | 0x0001 | 2 | cmcIIIDevType | 33024
InputRegister | ReadOnly | 1 | 3 | 0x0003 | 2 | cmcIIIDevSerial | 0x10001012
InputRegister | ReadOnly | 1 | 5 | 0x0005 | 2 | cmcIIIDevLastChange
InputRegister | ReadOnly | 1 | 7 | 0x0007 | 2 | cmcIIIDevLastChangeVars
InputRegister | ReadOnly | 1 | 9 | 0x0009 | 1 | cmcIIIDevNumberOfWritableVars
InputRegister | ReadOnly | 1 | 10 | 0x000A | 1 | cmcIIIDevNumberOfVars
InputRegister | ReadOnly | 1 | 11 | 0x000B | 1 | cmcIIIDevNumberOfMsgs
InputRegister | ReadOnly | 1 | 12 | 0x000C | 1 | cmcIIIDevStatus
InputRegister | ReadOnly | 1 | 13 | 0x000D | 128 | cmcIIIDevStatusText
InputRegister | ReadOnly | 1 | 141 | 0x008D | 3 | reserved
InputRegister | ReadOnly | 1 | 144 | 0x0090 | 2 | cmcIIIVarValueInt | Temperature.Offset 2
InputRegister | ReadOnly | 1 | 146 | 0x0092 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 148 | 0x0094 | 1 | cmcIIIVarType | 18
InputRegister | ReadOnly | 1 | 149 | 0x0095 | 32 | cmcIIIVarName | Temperature.Offset
InputRegister | ReadOnly | 1 | 181 | 0x00B5 | 3 | reserved
InputRegister | ReadOnly | 1 | 184 | 0x00B8 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 1 | 192 | 0x00C0 | 2 | cmcIIIVarMin | -1000
InputRegister | ReadOnly | 1 | 194 | 0x00C2 | 2 | cmcIIIVarMax | 1000
InputRegister | ReadOnly | 1 | 196 | 0x00C4 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 198 | 0x00C6 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 200 | 0x00C8 | 2 | reserved
InputRegister | ReadOnly | 1 | 202 | 0x00CA | 2 | cmcIIIVarValueInt | Temperature.SetPtHighAlarm 3
InputRegister | ReadOnly | 1 | 204 | 0x00CC | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 206 | 0x00CE | 1 | cmcIIIVarType | 3
InputRegister | ReadOnly | 1 | 207 | 0x00CF | 32 | cmcIIIVarName | Temperature.SetPtHighAlarm
InputRegister | ReadOnly | 1 | 239 | 0x00EF | 3 | reserved
InputRegister | ReadOnly | 1 | 242 | 0x00F2 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 1 | 250 | 0x00FA | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 1 | 252 | 0x00FC | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 1 | 254 | 0x00FE | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 256 | 0x0100 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 258 | 0x0102 | 2 | reserved
InputRegister | ReadOnly | 1 | 260 | 0x0104 | 2 | cmcIIIVarValueInt | Temperature.SetPtHighWarning 4
InputRegister | ReadOnly | 1 | 262 | 0x0106 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 264 | 0x0108 | 1 | cmcIIIVarType | 4
InputRegister | ReadOnly | 1 | 265 | 0x0109 | 32 | cmcIIIVarName | Temperature.SetPtHighWarning
InputRegister | ReadOnly | 1 | 297 | 0x0129 | 3 | reserved
InputRegister | ReadOnly | 1 | 300 | 0x012C | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 1 | 308 | 0x0134 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 1 | 310 | 0x0136 | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 1 | 312 | 0x0138 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 314 | 0x013A | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 316 | 0x013C | 2 | reserved
InputRegister | ReadOnly | 1 | 318 | 0x013E | 2 | cmcIIIVarValueInt | Temperature.SetPtLowWarning 5
InputRegister | ReadOnly | 1 | 320 | 0x0140 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 322 | 0x0142 | 1 | cmcIIIVarType | 9
InputRegister | ReadOnly | 1 | 323 | 0x0143 | 32 | cmcIIIVarName | Temperature.SetPtLowWarning
InputRegister | ReadOnly | 1 | 355 | 0x0163 | 3 | reserved
InputRegister | ReadOnly | 1 | 358 | 0x0166 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 1 | 366 | 0x016E | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 1 | 368 | 0x0170 | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 1 | 370 | 0x0172 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 372 | 0x0174 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 374 | 0x0176 | 2 | reserved
InputRegister | ReadOnly | 1 | 376 | 0x0178 | 2 | cmcIIIVarValueInt | Temperature.SetPtLowAlarm 6
InputRegister | ReadOnly | 1 | 378 | 0x017A | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 380 | 0x017C | 1 | cmcIIIVarType | 5
InputRegister | ReadOnly | 1 | 381 | 0x017D | 32 | cmcIIIVarName | Temperature.SetPtLowAlarm
InputRegister | ReadOnly | 1 | 413 | 0x019D | 3 | reserved
InputRegister | ReadOnly | 1 | 416 | 0x01A0 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 1 | 424 | 0x01A8 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 1 | 426 | 0x01AA | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 1 | 428 | 0x01AC | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 430 | 0x01AE | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 432 | 0x01B0 | 2 | reserved
InputRegister | ReadOnly | 1 | 434 | 0x01B2 | 2 | cmcIIIVarValueInt | Temperature.Hysteresis 7
InputRegister | ReadOnly | 1 | 436 | 0x01B4 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 438 | 0x01B6 | 1 | cmcIIIVarType | 6
InputRegister | ReadOnly | 1 | 439 | 0x01B7 | 32 | cmcIIIVarName | Temperature.Hysteresis
InputRegister | ReadOnly | 1 | 471 | 0x01D7 | 3 | reserved
InputRegister | ReadOnly | 1 | 474 | 0x01DA | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 1 | 482 | 0x01E2 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 484 | 0x01E4 | 2 | cmcIIIVarMax | 2000
InputRegister | ReadOnly | 1 | 486 | 0x01E6 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 488 | 0x01E8 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 490 | 0x01EA | 2 | reserved
InputRegister | ReadOnly | 1 | 492 | 0x01EC | 2 | cmcIIIVarValueInt | Temperature.Category 9
InputRegister | ReadOnly | 1 | 494 | 0x01EE | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 496 | 0x01F0 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 1 | 497 | 0x01F1 | 32 | cmcIIIVarName | Temperature.Category
InputRegister | ReadOnly | 1 | 529 | 0x0211 | 3 | reserved
InputRegister | ReadOnly | 1 | 532 | 0x0214 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 1 | 540 | 0x021C | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 542 | 0x021E | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 1 | 544 | 0x0220 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 546 | 0x0222 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 548 | 0x0224 | 2 | reserved
InputRegister | ReadOnly | 1 | 550 | 0x0226 | 2 | cmcIIIVarValueInt | System.CAN1 Current.SetPtHighAlarm 12
InputRegister | ReadOnly | 1 | 552 | 0x0228 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 554 | 0x022A | 1 | cmcIIIVarType | 3
InputRegister | ReadOnly | 1 | 555 | 0x022B | 32 | cmcIIIVarName | System.CAN1 Current.SetPtHighAlarm
InputRegister | ReadOnly | 1 | 587 | 0x024B | 3 | reserved
InputRegister | ReadOnly | 1 | 590 | 0x024E | 8 | cmcIIIVarUnit | mA
InputRegister | ReadOnly | 1 | 598 | 0x0256 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 600 | 0x0258 | 2 | cmcIIIVarMax | 2000
InputRegister | ReadOnly | 1 | 602 | 0x025A | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 604 | 0x025C | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 606 | 0x025E | 2 | reserved
InputRegister | ReadOnly | 1 | 608 | 0x0260 | 2 | cmcIIIVarValueInt | System.CAN1 Current.SetPtHighWarning 13
InputRegister | ReadOnly | 1 | 610 | 0x0262 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 612 | 0x0264 | 1 | cmcIIIVarType | 4
InputRegister | ReadOnly | 1 | 613 | 0x0265 | 32 | cmcIIIVarName | System.CAN1 Current.SetPtHighWarning
InputRegister | ReadOnly | 1 | 645 | 0x0285 | 3 | reserved
InputRegister | ReadOnly | 1 | 648 | 0x0288 | 8 | cmcIIIVarUnit | mA
InputRegister | ReadOnly | 1 | 656 | 0x0290 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 658 | 0x0292 | 2 | cmcIIIVarMax | 2000
InputRegister | ReadOnly | 1 | 660 | 0x0294 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 662 | 0x0296 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 664 | 0x0298 | 2 | reserved
InputRegister | ReadOnly | 1 | 666 | 0x029A | 2 | cmcIIIVarValueInt | System.CAN1 Current.Hysteresis 14
InputRegister | ReadOnly | 1 | 668 | 0x029C | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 670 | 0x029E | 1 | cmcIIIVarType | 6
InputRegister | ReadOnly | 1 | 671 | 0x029F | 32 | cmcIIIVarName | System.CAN1 Current.Hysteresis
InputRegister | ReadOnly | 1 | 703 | 0x02BF | 3 | reserved
InputRegister | ReadOnly | 1 | 706 | 0x02C2 | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 1 | 714 | 0x02CA | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 716 | 0x02CC | 2 | cmcIIIVarMax | 2000
InputRegister | ReadOnly | 1 | 718 | 0x02CE | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 720 | 0x02D0 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 722 | 0x02D2 | 2 | reserved
InputRegister | ReadOnly | 1 | 724 | 0x02D4 | 2 | cmcIIIVarValueInt | System.CAN1 Current.Category 16
InputRegister | ReadOnly | 1 | 726 | 0x02D6 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 728 | 0x02D8 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 1 | 729 | 0x02D9 | 32 | cmcIIIVarName | System.CAN1 Current.Category
InputRegister | ReadOnly | 1 | 761 | 0x02F9 | 3 | reserved
InputRegister | ReadOnly | 1 | 764 | 0x02FC | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 1 | 772 | 0x0304 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 774 | 0x0306 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 1 | 776 | 0x0308 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 778 | 0x030A | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 780 | 0x030C | 2 | reserved
InputRegister | ReadOnly | 1 | 782 | 0x030E | 2 | cmcIIIVarValueInt | System.CAN2 Current.SetPtHighAlarm 19
InputRegister | ReadOnly | 1 | 784 | 0x0310 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 786 | 0x0312 | 1 | cmcIIIVarType | 3
InputRegister | ReadOnly | 1 | 787 | 0x0313 | 32 | cmcIIIVarName | System.CAN2 Current.SetPtHighAlarm
InputRegister | ReadOnly | 1 | 819 | 0x0333 | 3 | reserved
InputRegister | ReadOnly | 1 | 822 | 0x0336 | 8 | cmcIIIVarUnit | mA
InputRegister | ReadOnly | 1 | 830 | 0x033E | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 832 | 0x0340 | 2 | cmcIIIVarMax | 2000
InputRegister | ReadOnly | 1 | 834 | 0x0342 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 836 | 0x0344 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 838 | 0x0346 | 2 | reserved
InputRegister | ReadOnly | 1 | 840 | 0x0348 | 2 | cmcIIIVarValueInt | System.CAN2 Current.SetPtHighWarning 20
InputRegister | ReadOnly | 1 | 842 | 0x034A | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 844 | 0x034C | 1 | cmcIIIVarType | 4
InputRegister | ReadOnly | 1 | 845 | 0x034D | 32 | cmcIIIVarName | System.CAN2 Current.SetPtHighWarning
InputRegister | ReadOnly | 1 | 877 | 0x036D | 3 | reserved
InputRegister | ReadOnly | 1 | 880 | 0x0370 | 8 | cmcIIIVarUnit | mA
InputRegister | ReadOnly | 1 | 888 | 0x0378 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 890 | 0x037A | 2 | cmcIIIVarMax | 2000
InputRegister | ReadOnly | 1 | 892 | 0x037C | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 894 | 0x037E | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 896 | 0x0380 | 2 | reserved
InputRegister | ReadOnly | 1 | 898 | 0x0382 | 2 | cmcIIIVarValueInt | System.CAN2 Current.Hysteresis 21
InputRegister | ReadOnly | 1 | 900 | 0x0384 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 902 | 0x0386 | 1 | cmcIIIVarType | 6
InputRegister | ReadOnly | 1 | 903 | 0x0387 | 32 | cmcIIIVarName | System.CAN2 Current.Hysteresis
InputRegister | ReadOnly | 1 | 935 | 0x03A7 | 3 | reserved
InputRegister | ReadOnly | 1 | 938 | 0x03AA | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 1 | 946 | 0x03B2 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 948 | 0x03B4 | 2 | cmcIIIVarMax | 2000
InputRegister | ReadOnly | 1 | 950 | 0x03B6 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 952 | 0x03B8 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 954 | 0x03BA | 2 | reserved
InputRegister | ReadOnly | 1 | 956 | 0x03BC | 2 | cmcIIIVarValueInt | System.CAN2 Current.Category 23
InputRegister | ReadOnly | 1 | 958 | 0x03BE | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 960 | 0x03C0 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 1 | 961 | 0x03C1 | 32 | cmcIIIVarName | System.CAN2 Current.Category
InputRegister | ReadOnly | 1 | 993 | 0x03E1 | 3 | reserved
InputRegister | ReadOnly | 1 | 996 | 0x03E4 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 1 | 1004 | 0x03EC | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 1006 | 0x03EE | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 1 | 1008 | 0x03F0 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 1010 | 0x03F2 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 1012 | 0x03F4 | 2 | reserved
InputRegister | ReadOnly | 1 | 1014 | 0x03F6 | 2 | cmcIIIVarValueInt | System.CAN Supply.Category 26
InputRegister | ReadOnly | 1 | 1016 | 0x03F8 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1018 | 0x03FA | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 1 | 1019 | 0x03FB | 32 | cmcIIIVarName | System.CAN Supply.Category
InputRegister | ReadOnly | 1 | 1051 | 0x041B | 3 | reserved
InputRegister | ReadOnly | 1 | 1054 | 0x041E | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 1 | 1062 | 0x0426 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 1064 | 0x0428 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 1 | 1066 | 0x042A | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 1068 | 0x042C | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 1070 | 0x042E | 2 | reserved
InputRegister | ReadOnly | 1 | 1072 | 0x0430 | 2 | cmcIIIVarValueInt | System.Supply 24V.Category 29
InputRegister | ReadOnly | 1 | 1074 | 0x0432 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1076 | 0x0434 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 1 | 1077 | 0x0435 | 32 | cmcIIIVarName | System.Supply 24V.Category
InputRegister | ReadOnly | 1 | 1109 | 0x0455 | 3 | reserved
InputRegister | ReadOnly | 1 | 1112 | 0x0458 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 1 | 1120 | 0x0460 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 1122 | 0x0462 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 1 | 1124 | 0x0464 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 1126 | 0x0466 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 1128 | 0x0468 | 2 | reserved
InputRegister | ReadOnly | 1 | 1130 | 0x046A | 2 | cmcIIIVarValueInt | System.Supply Cooling 1.Category 32
InputRegister | ReadOnly | 1 | 1132 | 0x046C | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1134 | 0x046E | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 1 | 1135 | 0x046F | 32 | cmcIIIVarName | System.Supply Cooling 1.Category
InputRegister | ReadOnly | 1 | 1167 | 0x048F | 3 | reserved
InputRegister | ReadOnly | 1 | 1170 | 0x0492 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 1 | 1178 | 0x049A | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 1180 | 0x049C | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 1 | 1182 | 0x049E | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 1184 | 0x04A0 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 1186 | 0x04A2 | 2 | reserved
InputRegister | ReadOnly | 1 | 1188 | 0x04A4 | 2 | cmcIIIVarValueInt | Memory.USB-Stick.Command 36
InputRegister | ReadOnly | 1 | 1190 | 0x04A6 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1192 | 0x04A8 | 1 | cmcIIIVarType | 81
InputRegister | ReadOnly | 1 | 1193 | 0x04A9 | 32 | cmcIIIVarName | Memory.USB-Stick.Command
InputRegister | ReadOnly | 1 | 1225 | 0x04C9 | 32 | cmcIIIVarConstraints | 4,9
InputRegister | ReadOnly | 1 | 1257 | 0x04E9 | 2 | reserved
InputRegister | ReadOnly | 1 | 1259 | 0x04EB | 2 | cmcIIIVarValueInt | Memory.USB-Stick.Category 38
InputRegister | ReadOnly | 1 | 1261 | 0x04ED | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1263 | 0x04EF | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 1 | 1264 | 0x04F0 | 32 | cmcIIIVarName | Memory.USB-Stick.Category
InputRegister | ReadOnly | 1 | 1296 | 0x0510 | 3 | reserved
InputRegister | ReadOnly | 1 | 1299 | 0x0513 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 1 | 1307 | 0x051B | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 1309 | 0x051D | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 1 | 1311 | 0x051F | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 1313 | 0x0521 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 1315 | 0x0523 | 2 | reserved
InputRegister | ReadOnly | 1 | 1317 | 0x0525 | 2 | cmcIIIVarValueInt | Memory.SD-Card.Command 42
InputRegister | ReadOnly | 1 | 1319 | 0x0527 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1321 | 0x0529 | 1 | cmcIIIVarType | 81
InputRegister | ReadOnly | 1 | 1322 | 0x052A | 32 | cmcIIIVarName | Memory.SD-Card.Command
InputRegister | ReadOnly | 1 | 1354 | 0x054A | 32 | cmcIIIVarConstraints | 4,9
InputRegister | ReadOnly | 1 | 1386 | 0x056A | 2 | reserved
InputRegister | ReadOnly | 1 | 1388 | 0x056C | 2 | cmcIIIVarValueInt | Memory.SD-Card.Category 44
InputRegister | ReadOnly | 1 | 1390 | 0x056E | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1392 | 0x0570 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 1 | 1393 | 0x0571 | 32 | cmcIIIVarName | Memory.SD-Card.Category
InputRegister | ReadOnly | 1 | 1425 | 0x0591 | 3 | reserved
InputRegister | ReadOnly | 1 | 1428 | 0x0594 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 1 | 1436 | 0x059C | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 1438 | 0x059E | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 1 | 1440 | 0x05A0 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 1442 | 0x05A2 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 1444 | 0x05A4 | 2 | reserved
InputRegister | ReadOnly | 1 | 1446 | 0x05A6 | 2 | cmcIIIVarValueInt | Webcam.Command 46
InputRegister | ReadOnly | 1 | 1448 | 0x05A8 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1450 | 0x05AA | 1 | cmcIIIVarType | 81
InputRegister | ReadOnly | 1 | 1451 | 0x05AB | 32 | cmcIIIVarName | Webcam.Command
InputRegister | ReadOnly | 1 | 1483 | 0x05CB | 32 | cmcIIIVarConstraints | 4,10
InputRegister | ReadOnly | 1 | 1515 | 0x05EB | 2 | reserved
InputRegister | ReadOnly | 1 | 1517 | 0x05ED | 2 | cmcIIIVarValueInt | Webcam.Category 48
InputRegister | ReadOnly | 1 | 1519 | 0x05EF | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1521 | 0x05F1 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 1 | 1522 | 0x05F2 | 32 | cmcIIIVarName | Webcam.Category
InputRegister | ReadOnly | 1 | 1554 | 0x0612 | 3 | reserved
InputRegister | ReadOnly | 1 | 1557 | 0x0615 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 1 | 1565 | 0x061D | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 1567 | 0x061F | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 1 | 1569 | 0x0621 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 1571 | 0x0623 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 1573 | 0x0625 | 2 | reserved
InputRegister | ReadOnly | 1 | 1575 | 0x0627 | 2 | cmcIIIVarValueInt | Temperature.Value 1
InputRegister | ReadOnly | 1 | 1577 | 0x0629 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1579 | 0x062B | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 1 | 1580 | 0x062C | 32 | cmcIIIVarName | Temperature.Value
InputRegister | ReadOnly | 1 | 1612 | 0x064C | 3 | reserved
InputRegister | ReadOnly | 1 | 1615 | 0x064F | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 1 | 1623 | 0x0657 | 2 | cmcIIIVarMin | -4000
InputRegister | ReadOnly | 1 | 1625 | 0x0659 | 2 | cmcIIIVarMax | 9000
InputRegister | ReadOnly | 1 | 1627 | 0x065B | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 1629 | 0x065D | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 1631 | 0x065F | 2 | reserved
InputRegister | ReadOnly | 1 | 1633 | 0x0661 | 2 | cmcIIIVarValueInt | Temperature.Status 8
InputRegister | ReadOnly | 1 | 1635 | 0x0663 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1637 | 0x0665 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 1 | 1638 | 0x0666 | 32 | cmcIIIVarName | Temperature.Status
InputRegister | ReadOnly | 1 | 1670 | 0x0686 | 32 | cmcIIIVarConstraints | 1,4,6,7,8,9,24,25
InputRegister | ReadOnly | 1 | 1702 | 0x06A6 | 2 | reserved
InputRegister | ReadOnly | 1 | 1704 | 0x06A8 | 2 | cmcIIIVarValueInt | System.CAN1 Current.Value 11
InputRegister | ReadOnly | 1 | 1706 | 0x06AA | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1708 | 0x06AC | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 1 | 1709 | 0x06AD | 32 | cmcIIIVarName | System.CAN1 Current.Value
InputRegister | ReadOnly | 1 | 1741 | 0x06CD | 3 | reserved
InputRegister | ReadOnly | 1 | 1744 | 0x06D0 | 8 | cmcIIIVarUnit | mA
InputRegister | ReadOnly | 1 | 1752 | 0x06D8 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 1754 | 0x06DA | 2 | cmcIIIVarMax | 3000
InputRegister | ReadOnly | 1 | 1756 | 0x06DC | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 1758 | 0x06DE | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 1760 | 0x06E0 | 2 | reserved
InputRegister | ReadOnly | 1 | 1762 | 0x06E2 | 2 | cmcIIIVarValueInt | System.CAN1 Current.Status 15
InputRegister | ReadOnly | 1 | 1764 | 0x06E4 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1766 | 0x06E6 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 1 | 1767 | 0x06E7 | 32 | cmcIIIVarName | System.CAN1 Current.Status
InputRegister | ReadOnly | 1 | 1799 | 0x0707 | 32 | cmcIIIVarConstraints | 1,4,6,8
InputRegister | ReadOnly | 1 | 1831 | 0x0727 | 2 | reserved
InputRegister | ReadOnly | 1 | 1833 | 0x0729 | 2 | cmcIIIVarValueInt | System.CAN2 Current.Value 18
InputRegister | ReadOnly | 1 | 1835 | 0x072B | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1837 | 0x072D | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 1 | 1838 | 0x072E | 32 | cmcIIIVarName | System.CAN2 Current.Value
InputRegister | ReadOnly | 1 | 1870 | 0x074E | 3 | reserved
InputRegister | ReadOnly | 1 | 1873 | 0x0751 | 8 | cmcIIIVarUnit | mA
InputRegister | ReadOnly | 1 | 1881 | 0x0759 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 1883 | 0x075B | 2 | cmcIIIVarMax | 3000
InputRegister | ReadOnly | 1 | 1885 | 0x075D | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 1 | 1887 | 0x075F | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 1 | 1889 | 0x0761 | 2 | reserved
InputRegister | ReadOnly | 1 | 1891 | 0x0763 | 2 | cmcIIIVarValueInt | System.CAN2 Current.Status 22
InputRegister | ReadOnly | 1 | 1893 | 0x0765 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1895 | 0x0767 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 1 | 1896 | 0x0768 | 32 | cmcIIIVarName | System.CAN2 Current.Status
InputRegister | ReadOnly | 1 | 1928 | 0x0788 | 32 | cmcIIIVarConstraints | 1,4,6,8
InputRegister | ReadOnly | 1 | 1960 | 0x07A8 | 2 | reserved
InputRegister | ReadOnly | 1 | 1962 | 0x07AA | 2 | cmcIIIVarValueInt | System.CAN Supply.Status 25
InputRegister | ReadOnly | 1 | 1964 | 0x07AC | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 1966 | 0x07AE | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 1 | 1967 | 0x07AF | 32 | cmcIIIVarName | System.CAN Supply.Status
InputRegister | ReadOnly | 1 | 1999 | 0x07CF | 32 | cmcIIIVarConstraints | 1,3,4
InputRegister | ReadOnly | 1 | 2031 | 0x07EF | 2 | reserved
InputRegister | ReadOnly | 1 | 2033 | 0x07F1 | 2 | cmcIIIVarValueInt | System.Supply 24V.Status 28
InputRegister | ReadOnly | 1 | 2035 | 0x07F3 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 2037 | 0x07F5 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 1 | 2038 | 0x07F6 | 32 | cmcIIIVarName | System.Supply 24V.Status
InputRegister | ReadOnly | 1 | 2070 | 0x0816 | 32 | cmcIIIVarConstraints | 1,4
InputRegister | ReadOnly | 1 | 2102 | 0x0836 | 2 | reserved
InputRegister | ReadOnly | 1 | 2104 | 0x0838 | 2 | cmcIIIVarValueInt | System.Supply Cooling 1.Status 31
InputRegister | ReadOnly | 1 | 2106 | 0x083A | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 2108 | 0x083C | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 1 | 2109 | 0x083D | 32 | cmcIIIVarName | System.Supply Cooling 1.Status
InputRegister | ReadOnly | 1 | 2141 | 0x085D | 32 | cmcIIIVarConstraints | 1,4
InputRegister | ReadOnly | 1 | 2173 | 0x087D | 2 | reserved
InputRegister | ReadOnly | 1 | 2175 | 0x087F | 2 | cmcIIIVarValueInt | Memory.USB-Stick.Size 34
InputRegister | ReadOnly | 1 | 2177 | 0x0881 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 2179 | 0x0883 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 1 | 2180 | 0x0884 | 32 | cmcIIIVarName | Memory.USB-Stick.Size
InputRegister | ReadOnly | 1 | 2212 | 0x08A4 | 3 | reserved
InputRegister | ReadOnly | 1 | 2215 | 0x08A7 | 8 | cmcIIIVarUnit | GB
InputRegister | ReadOnly | 1 | 2223 | 0x08AF | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 2225 | 0x08B1 | 2 | cmcIIIVarMax | 9999
InputRegister | ReadOnly | 1 | 2227 | 0x08B3 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 2229 | 0x08B5 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 2231 | 0x08B7 | 2 | reserved
InputRegister | ReadOnly | 1 | 2233 | 0x08B9 | 2 | cmcIIIVarValueInt | Memory.USB-Stick.Usage 35
InputRegister | ReadOnly | 1 | 2235 | 0x08BB | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 2237 | 0x08BD | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 1 | 2238 | 0x08BE | 32 | cmcIIIVarName | Memory.USB-Stick.Usage
InputRegister | ReadOnly | 1 | 2270 | 0x08DE | 3 | reserved
InputRegister | ReadOnly | 1 | 2273 | 0x08E1 | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 1 | 2281 | 0x08E9 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 2283 | 0x08EB | 2 | cmcIIIVarMax | 100
InputRegister | ReadOnly | 1 | 2285 | 0x08ED | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 2287 | 0x08EF | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 2289 | 0x08F1 | 2 | reserved
InputRegister | ReadOnly | 1 | 2291 | 0x08F3 | 2 | cmcIIIVarValueInt | Memory.USB-Stick.Status 37
InputRegister | ReadOnly | 1 | 2293 | 0x08F5 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 2295 | 0x08F7 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 1 | 2296 | 0x08F8 | 32 | cmcIIIVarName | Memory.USB-Stick.Status
InputRegister | ReadOnly | 1 | 2328 | 0x0918 | 32 | cmcIIIVarConstraints | 1,4,6,8,27,30
InputRegister | ReadOnly | 1 | 2360 | 0x0938 | 2 | reserved
InputRegister | ReadOnly | 1 | 2362 | 0x093A | 2 | cmcIIIVarValueInt | Memory.SD-Card.Size 40
InputRegister | ReadOnly | 1 | 2364 | 0x093C | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 2366 | 0x093E | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 1 | 2367 | 0x093F | 32 | cmcIIIVarName | Memory.SD-Card.Size
InputRegister | ReadOnly | 1 | 2399 | 0x095F | 3 | reserved
InputRegister | ReadOnly | 1 | 2402 | 0x0962 | 8 | cmcIIIVarUnit | GB
InputRegister | ReadOnly | 1 | 2410 | 0x096A | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 2412 | 0x096C | 2 | cmcIIIVarMax | 9999
InputRegister | ReadOnly | 1 | 2414 | 0x096E | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 2416 | 0x0970 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 2418 | 0x0972 | 2 | reserved
InputRegister | ReadOnly | 1 | 2420 | 0x0974 | 2 | cmcIIIVarValueInt | Memory.SD-Card.Usage 41
InputRegister | ReadOnly | 1 | 2422 | 0x0976 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 2424 | 0x0978 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 1 | 2425 | 0x0979 | 32 | cmcIIIVarName | Memory.SD-Card.Usage
InputRegister | ReadOnly | 1 | 2457 | 0x0999 | 3 | reserved
InputRegister | ReadOnly | 1 | 2460 | 0x099C | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 1 | 2468 | 0x09A4 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 1 | 2470 | 0x09A6 | 2 | cmcIIIVarMax | 100
InputRegister | ReadOnly | 1 | 2472 | 0x09A8 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 1 | 2474 | 0x09AA | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 1 | 2476 | 0x09AC | 2 | reserved
InputRegister | ReadOnly | 1 | 2478 | 0x09AE | 2 | cmcIIIVarValueInt | Memory.SD-Card.Status 43
InputRegister | ReadOnly | 1 | 2480 | 0x09B0 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 2482 | 0x09B2 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 1 | 2483 | 0x09B3 | 32 | cmcIIIVarName | Memory.SD-Card.Status
InputRegister | ReadOnly | 1 | 2515 | 0x09D3 | 32 | cmcIIIVarConstraints | 1,4,6,8,27,30
InputRegister | ReadOnly | 1 | 2547 | 0x09F3 | 2 | reserved
InputRegister | ReadOnly | 1 | 2549 | 0x09F5 | 2 | cmcIIIVarValueInt | Webcam.Status 47
InputRegister | ReadOnly | 1 | 2551 | 0x09F7 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 1 | 2553 | 0x09F9 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 1 | 2554 | 0x09FA | 32 | cmcIIIVarName | Webcam.Status
InputRegister | ReadOnly | 1 | 2586 | 0x0A1A | 32 | cmcIIIVarConstraints | 1,4,5,19
InputRegister | ReadOnly | 1 | 2618 | 0x0A3A | 2 | reserved
DeviceIdentification | ReadOnly | 1 | 0 | 0x00 | 10 | vendor name | Rittal GmbH & Co. KG
DeviceIdentification | ReadOnly | 1 | 1 | 0x01 | 2 | product code | CMC
DeviceIdentification | ReadOnly | 1 | 2 | 0x02 | 2 | major.minor version | 1.04
DeviceIdentification | ReadOnly | 1 | 3 | 0x03 | 11 | vendor URL | http://www.rittal.com
DeviceIdentification | ReadOnly | 1 | 4 | 0x04 | 32 | product name | CMCIII
DeviceIdentification | ReadOnly | 1 | 5 | 0x05 | 32 | model name | Computer Multi Control III
DeviceIdentification | ReadOnly | 1 | 6 | 0x06 | 4 | application name | cmc3mbd
DeviceIdentification | ReadOnly | 1 | 128 | 0x80 | 9 | mac address | 10:CE:A9:A5:6D:BD
DeviceIdentification | ReadOnly | 1 | 129 | 0x81 | 5 | cmcIIIDevSerial | 0x10001012
DeviceIdentification | ReadOnly | 1 | 130 | 0x82 | 32 | cmcIIIDevName | IoT Interface
DeviceIdentification | ReadOnly | 1 | 131 | 0x83 | 16 | cmcIIIDevArtNr | 3124.3
DeviceIdentification | ReadOnly | 1 | 132 | 0x84 | 16 | cmcIIIDevFW | V6.15.70
DeviceIdentification | ReadOnly | 1 | 133 | 0x85 | 16 | cmcIIIDevHW | V1.0.2
DeviceIdentification | ReadOnly | 1 | 134 | 0x86 | 16 | cmcIIIUnitOSRev | 4.14.78-ge7405910ca
DeviceIdentification | ReadOnly | 1 | 135 | 0x87 | 4 | cmcIIIDevProductWeek | 12/2019
DeviceIdentification | ReadOnly | 1 | 136 | 0x88 | 32 | cmcIIIDevAlias | IoT Interface
DeviceIdentification | ReadOnly | 1 | 137 | 0x89 | 32 | cmcIIIDevLocation | Location
DeviceIdentification | ReadOnly | 1 | 138 | 0x8A | 64 | cmcIIIDevAssembly
HoldingRegister | ReadWrite | 2 | 0 | 0x0000 | 2 | cmcIIIVarValueInt | Internal Temperature.SetPtHighAlarm 9
HoldingRegister | ReadWrite | 2 | 2 | 0x0002 | 2 | cmcIIIVarValueInt | Internal Temperature.SetPtHighWarning 10
HoldingRegister | ReadWrite | 2 | 4 | 0x0004 | 2 | cmcIIIVarValueInt | Internal Temperature.SetPtLowWarning 11
HoldingRegister | ReadWrite | 2 | 6 | 0x0006 | 2 | cmcIIIVarValueInt | Internal Temperature.SetPtLowAlarm 12
HoldingRegister | ReadWrite | 2 | 8 | 0x0008 | 2 | cmcIIIVarValueInt | Internal Temperature.Hysteresis 13
HoldingRegister | ReadWrite | 2 | 10 | 0x000A | 2 | cmcIIIVarValueInt | Internal Temperature.Category 16
HoldingRegister | ReadWrite | 2 | 12 | 0x000C | 2 | cmcIIIVarValueInt | Ambient Temperature.SetPtHighAlarm 19
HoldingRegister | ReadWrite | 2 | 14 | 0x000E | 2 | cmcIIIVarValueInt | Ambient Temperature.SetPtHighWarning 20
HoldingRegister | ReadWrite | 2 | 16 | 0x0010 | 2 | cmcIIIVarValueInt | Ambient Temperature.SetPtLowWarning 21
HoldingRegister | ReadWrite | 2 | 18 | 0x0012 | 2 | cmcIIIVarValueInt | Ambient Temperature.SetPtLowAlarm 22
HoldingRegister | ReadWrite | 2 | 20 | 0x0014 | 2 | cmcIIIVarValueInt | Ambient Temperature.Hysteresis 23
HoldingRegister | ReadWrite | 2 | 22 | 0x0016 | 2 | cmcIIIVarValueInt | Ambient Temperature.Category 26
HoldingRegister | ReadWrite | 2 | 24 | 0x0018 | 2 | cmcIIIVarValueInt | External Temperature Sensor.SetPtHighAlarm 29
HoldingRegister | ReadWrite | 2 | 26 | 0x001A | 2 | cmcIIIVarValueInt | External Temperature Sensor.SetPtHighWarning 30
HoldingRegister | ReadWrite | 2 | 28 | 0x001C | 2 | cmcIIIVarValueInt | External Temperature Sensor.SetPtLowWarning 31
HoldingRegister | ReadWrite | 2 | 30 | 0x001E | 2 | cmcIIIVarValueInt | External Temperature Sensor.SetPtLowAlarm 32
HoldingRegister | ReadWrite | 2 | 32 | 0x0020 | 2 | cmcIIIVarValueInt | External Temperature Sensor.Hysteresis 33
HoldingRegister | ReadWrite | 2 | 34 | 0x0022 | 2 | cmcIIIVarValueInt | External Temperature Sensor.Category 36
HoldingRegister | ReadWrite | 2 | 36 | 0x0024 | 2 | cmcIIIVarValueInt | Monitoring.Cooling.Category 47
HoldingRegister | ReadWrite | 2 | 38 | 0x0026 | 2 | cmcIIIVarValueInt | Monitoring.Internal Air Circuit.Category 52
HoldingRegister | ReadWrite | 2 | 40 | 0x0028 | 2 | cmcIIIVarValueInt | Monitoring.External Air Circuit.Category 57
HoldingRegister | ReadWrite | 2 | 42 | 0x002A | 2 | cmcIIIVarValueInt | Monitoring.Internal Fan.Category 63
HoldingRegister | ReadWrite | 2 | 44 | 0x002C | 2 | cmcIIIVarValueInt | Monitoring.External Fan.Category 69
HoldingRegister | ReadWrite | 2 | 46 | 0x002E | 2 | cmcIIIVarValueInt | Monitoring.Compressor.Category 75
HoldingRegister | ReadWrite | 2 | 48 | 0x0030 | 2 | cmcIIIVarValueInt | Monitoring.EEV.Category 81
HoldingRegister | ReadWrite | 2 | 50 | 0x0032 | 2 | cmcIIIVarValueInt | Monitoring.Filter.Category 85
HoldingRegister | ReadWrite | 2 | 52 | 0x0034 | 2 | cmcIIIVarValueInt | Monitoring.Door.Category 89
HoldingRegister | ReadWrite | 2 | 54 | 0x0036 | 2 | cmcIIIVarValueInt | Monitoring.Electronics.Category 93
HoldingRegister | ReadWrite | 2 | 56 | 0x0038 | 2 | cmcIIIVarValueInt | Monitoring.Condensate.Category 97
HoldingRegister | ReadWrite | 2 | 58 | 0x003A | 2 | cmcIIIVarValueInt | Monitoring.System Messages.Category 101
HoldingRegister | ReadWrite | 2 | 60 | 0x003C | 2 | cmcIIIVarValueInt | Setup.Mode 115
HoldingRegister | ReadWrite | 2 | 62 | 0x003E | 2 | cmcIIIVarValueInt | Setup.Alarm Tolerance Filter 116
HoldingRegister | ReadWrite | 2 | 64 | 0x0040 | 2 | cmcIIIVarValueInt | Setup.Standard Control.Setpoint 117
HoldingRegister | ReadWrite | 2 | 66 | 0x0042 | 2 | cmcIIIVarValueInt | Setup.Standard Control.Alarm Threshold 118
HoldingRegister | ReadWrite | 2 | 68 | 0x0044 | 2 | cmcIIIVarValueInt | Setup.Outlet Temperature.Setpoint 119
HoldingRegister | ReadWrite | 2 | 70 | 0x0046 | 2 | cmcIIIVarValueInt | Setup.Outlet Temperature.Alarm Threshold 120
InputRegister | ReadOnly | 2 | 0 | 0x0000 | 1 | cmcIIIDevIndex | 2
InputRegister | ReadOnly | 2 | 1 | 0x0001 | 2 | cmcIIIDevType | 24832
InputRegister | ReadOnly | 2 | 3 | 0x0003 | 2 | cmcIIIDevSerial | 0x00135177
InputRegister | ReadOnly | 2 | 5 | 0x0005 | 2 | cmcIIIDevLastChange
InputRegister | ReadOnly | 2 | 7 | 0x0007 | 2 | cmcIIIDevLastChangeVars
InputRegister | ReadOnly | 2 | 9 | 0x0009 | 1 | cmcIIIDevNumberOfWritableVars
InputRegister | ReadOnly | 2 | 10 | 0x000A | 1 | cmcIIIDevNumberOfVars
InputRegister | ReadOnly | 2 | 11 | 0x000B | 1 | cmcIIIDevNumberOfMsgs
InputRegister | ReadOnly | 2 | 12 | 0x000C | 1 | cmcIIIDevStatus
InputRegister | ReadOnly | 2 | 13 | 0x000D | 128 | cmcIIIDevStatusText
InputRegister | ReadOnly | 2 | 141 | 0x008D | 3 | reserved
InputRegister | ReadOnly | 2 | 144 | 0x0090 | 2 | cmcIIIVarValueInt | Internal Temperature.SetPtHighAlarm 9
InputRegister | ReadOnly | 2 | 146 | 0x0092 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 148 | 0x0094 | 1 | cmcIIIVarType | 3
InputRegister | ReadOnly | 2 | 149 | 0x0095 | 32 | cmcIIIVarName | Internal Temperature.SetPtHighAlarm
InputRegister | ReadOnly | 2 | 181 | 0x00B5 | 3 | reserved
InputRegister | ReadOnly | 2 | 184 | 0x00B8 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 192 | 0x00C0 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 194 | 0x00C2 | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 196 | 0x00C4 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 198 | 0x00C6 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 200 | 0x00C8 | 2 | reserved
InputRegister | ReadOnly | 2 | 202 | 0x00CA | 2 | cmcIIIVarValueInt | Internal Temperature.SetPtHighWarning 10
InputRegister | ReadOnly | 2 | 204 | 0x00CC | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 206 | 0x00CE | 1 | cmcIIIVarType | 4
InputRegister | ReadOnly | 2 | 207 | 0x00CF | 32 | cmcIIIVarName | Internal Temperature.SetPtHighWarning
InputRegister | ReadOnly | 2 | 239 | 0x00EF | 3 | reserved
InputRegister | ReadOnly | 2 | 242 | 0x00F2 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 250 | 0x00FA | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 252 | 0x00FC | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 254 | 0x00FE | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 256 | 0x0100 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 258 | 0x0102 | 2 | reserved
InputRegister | ReadOnly | 2 | 260 | 0x0104 | 2 | cmcIIIVarValueInt | Internal Temperature.SetPtLowWarning 11
InputRegister | ReadOnly | 2 | 262 | 0x0106 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 264 | 0x0108 | 1 | cmcIIIVarType | 9
InputRegister | ReadOnly | 2 | 265 | 0x0109 | 32 | cmcIIIVarName | Internal Temperature.SetPtLowWarning
InputRegister | ReadOnly | 2 | 297 | 0x0129 | 3 | reserved
InputRegister | ReadOnly | 2 | 300 | 0x012C | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 308 | 0x0134 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 310 | 0x0136 | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 312 | 0x0138 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 314 | 0x013A | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 316 | 0x013C | 2 | reserved
InputRegister | ReadOnly | 2 | 318 | 0x013E | 2 | cmcIIIVarValueInt | Internal Temperature.SetPtLowAlarm 12
InputRegister | ReadOnly | 2 | 320 | 0x0140 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 322 | 0x0142 | 1 | cmcIIIVarType | 5
InputRegister | ReadOnly | 2 | 323 | 0x0143 | 32 | cmcIIIVarName | Internal Temperature.SetPtLowAlarm
InputRegister | ReadOnly | 2 | 355 | 0x0163 | 3 | reserved
InputRegister | ReadOnly | 2 | 358 | 0x0166 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 366 | 0x016E | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 368 | 0x0170 | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 370 | 0x0172 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 372 | 0x0174 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 374 | 0x0176 | 2 | reserved
InputRegister | ReadOnly | 2 | 376 | 0x0178 | 2 | cmcIIIVarValueInt | Internal Temperature.Hysteresis 13
InputRegister | ReadOnly | 2 | 378 | 0x017A | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 380 | 0x017C | 1 | cmcIIIVarType | 6
InputRegister | ReadOnly | 2 | 381 | 0x017D | 32 | cmcIIIVarName | Internal Temperature.Hysteresis
InputRegister | ReadOnly | 2 | 413 | 0x019D | 3 | reserved
InputRegister | ReadOnly | 2 | 416 | 0x01A0 | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 2 | 424 | 0x01A8 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 426 | 0x01AA | 2 | cmcIIIVarMax | 2000
InputRegister | ReadOnly | 2 | 428 | 0x01AC | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 430 | 0x01AE | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 432 | 0x01B0 | 2 | reserved
InputRegister | ReadOnly | 2 | 434 | 0x01B2 | 2 | cmcIIIVarValueInt | Internal Temperature.Category 16
InputRegister | ReadOnly | 2 | 436 | 0x01B4 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 438 | 0x01B6 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 439 | 0x01B7 | 32 | cmcIIIVarName | Internal Temperature.Category
InputRegister | ReadOnly | 2 | 471 | 0x01D7 | 3 | reserved
InputRegister | ReadOnly | 2 | 474 | 0x01DA | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 482 | 0x01E2 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 484 | 0x01E4 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 486 | 0x01E6 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 488 | 0x01E8 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 490 | 0x01EA | 2 | reserved
InputRegister | ReadOnly | 2 | 492 | 0x01EC | 2 | cmcIIIVarValueInt | Ambient Temperature.SetPtHighAlarm 19
InputRegister | ReadOnly | 2 | 494 | 0x01EE | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 496 | 0x01F0 | 1 | cmcIIIVarType | 3
InputRegister | ReadOnly | 2 | 497 | 0x01F1 | 32 | cmcIIIVarName | Ambient Temperature.SetPtHighAlarm
InputRegister | ReadOnly | 2 | 529 | 0x0211 | 3 | reserved
InputRegister | ReadOnly | 2 | 532 | 0x0214 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 540 | 0x021C | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 542 | 0x021E | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 544 | 0x0220 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 546 | 0x0222 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 548 | 0x0224 | 2 | reserved
InputRegister | ReadOnly | 2 | 550 | 0x0226 | 2 | cmcIIIVarValueInt | Ambient Temperature.SetPtHighWarning 20
InputRegister | ReadOnly | 2 | 552 | 0x0228 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 554 | 0x022A | 1 | cmcIIIVarType | 4
InputRegister | ReadOnly | 2 | 555 | 0x022B | 32 | cmcIIIVarName | Ambient Temperature.SetPtHighWarning
InputRegister | ReadOnly | 2 | 587 | 0x024B | 3 | reserved
InputRegister | ReadOnly | 2 | 590 | 0x024E | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 598 | 0x0256 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 600 | 0x0258 | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 602 | 0x025A | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 604 | 0x025C | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 606 | 0x025E | 2 | reserved
InputRegister | ReadOnly | 2 | 608 | 0x0260 | 2 | cmcIIIVarValueInt | Ambient Temperature.SetPtLowWarning 21
InputRegister | ReadOnly | 2 | 610 | 0x0262 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 612 | 0x0264 | 1 | cmcIIIVarType | 9
InputRegister | ReadOnly | 2 | 613 | 0x0265 | 32 | cmcIIIVarName | Ambient Temperature.SetPtLowWarning
InputRegister | ReadOnly | 2 | 645 | 0x0285 | 3 | reserved
InputRegister | ReadOnly | 2 | 648 | 0x0288 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 656 | 0x0290 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 658 | 0x0292 | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 660 | 0x0294 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 662 | 0x0296 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 664 | 0x0298 | 2 | reserved
InputRegister | ReadOnly | 2 | 666 | 0x029A | 2 | cmcIIIVarValueInt | Ambient Temperature.SetPtLowAlarm 22
InputRegister | ReadOnly | 2 | 668 | 0x029C | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 670 | 0x029E | 1 | cmcIIIVarType | 5
InputRegister | ReadOnly | 2 | 671 | 0x029F | 32 | cmcIIIVarName | Ambient Temperature.SetPtLowAlarm
InputRegister | ReadOnly | 2 | 703 | 0x02BF | 3 | reserved
InputRegister | ReadOnly | 2 | 706 | 0x02C2 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 714 | 0x02CA | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 716 | 0x02CC | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 718 | 0x02CE | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 720 | 0x02D0 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 722 | 0x02D2 | 2 | reserved
InputRegister | ReadOnly | 2 | 724 | 0x02D4 | 2 | cmcIIIVarValueInt | Ambient Temperature.Hysteresis 23
InputRegister | ReadOnly | 2 | 726 | 0x02D6 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 728 | 0x02D8 | 1 | cmcIIIVarType | 6
InputRegister | ReadOnly | 2 | 729 | 0x02D9 | 32 | cmcIIIVarName | Ambient Temperature.Hysteresis
InputRegister | ReadOnly | 2 | 761 | 0x02F9 | 3 | reserved
InputRegister | ReadOnly | 2 | 764 | 0x02FC | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 2 | 772 | 0x0304 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 774 | 0x0306 | 2 | cmcIIIVarMax | 2000
InputRegister | ReadOnly | 2 | 776 | 0x0308 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 778 | 0x030A | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 780 | 0x030C | 2 | reserved
InputRegister | ReadOnly | 2 | 782 | 0x030E | 2 | cmcIIIVarValueInt | Ambient Temperature.Category 26
InputRegister | ReadOnly | 2 | 784 | 0x0310 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 786 | 0x0312 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 787 | 0x0313 | 32 | cmcIIIVarName | Ambient Temperature.Category
InputRegister | ReadOnly | 2 | 819 | 0x0333 | 3 | reserved
InputRegister | ReadOnly | 2 | 822 | 0x0336 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 830 | 0x033E | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 832 | 0x0340 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 834 | 0x0342 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 836 | 0x0344 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 838 | 0x0346 | 2 | reserved
InputRegister | ReadOnly | 2 | 840 | 0x0348 | 2 | cmcIIIVarValueInt | External Temperature Sensor.SetPtHighAlarm 29
InputRegister | ReadOnly | 2 | 842 | 0x034A | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 844 | 0x034C | 1 | cmcIIIVarType | 3
InputRegister | ReadOnly | 2 | 845 | 0x034D | 32 | cmcIIIVarName | External Temperature Sensor.SetPtHighAlarm
InputRegister | ReadOnly | 2 | 877 | 0x036D | 3 | reserved
InputRegister | ReadOnly | 2 | 880 | 0x0370 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 888 | 0x0378 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 890 | 0x037A | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 892 | 0x037C | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 894 | 0x037E | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 896 | 0x0380 | 2 | reserved
InputRegister | ReadOnly | 2 | 898 | 0x0382 | 2 | cmcIIIVarValueInt | External Temperature Sensor.SetPtHighWarning 30
InputRegister | ReadOnly | 2 | 900 | 0x0384 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 902 | 0x0386 | 1 | cmcIIIVarType | 4
InputRegister | ReadOnly | 2 | 903 | 0x0387 | 32 | cmcIIIVarName | External Temperature Sensor.SetPtHighWarning
InputRegister | ReadOnly | 2 | 935 | 0x03A7 | 3 | reserved
InputRegister | ReadOnly | 2 | 938 | 0x03AA | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 946 | 0x03B2 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 948 | 0x03B4 | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 950 | 0x03B6 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 952 | 0x03B8 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 954 | 0x03BA | 2 | reserved
InputRegister | ReadOnly | 2 | 956 | 0x03BC | 2 | cmcIIIVarValueInt | External Temperature Sensor.SetPtLowWarning 31
InputRegister | ReadOnly | 2 | 958 | 0x03BE | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 960 | 0x03C0 | 1 | cmcIIIVarType | 9
InputRegister | ReadOnly | 2 | 961 | 0x03C1 | 32 | cmcIIIVarName | External Temperature Sensor.SetPtLowWarning
InputRegister | ReadOnly | 2 | 993 | 0x03E1 | 3 | reserved
InputRegister | ReadOnly | 2 | 996 | 0x03E4 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 1004 | 0x03EC | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 1006 | 0x03EE | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 1008 | 0x03F0 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 1010 | 0x03F2 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 1012 | 0x03F4 | 2 | reserved
InputRegister | ReadOnly | 2 | 1014 | 0x03F6 | 2 | cmcIIIVarValueInt | External Temperature Sensor.SetPtLowAlarm 32
InputRegister | ReadOnly | 2 | 1016 | 0x03F8 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1018 | 0x03FA | 1 | cmcIIIVarType | 5
InputRegister | ReadOnly | 2 | 1019 | 0x03FB | 32 | cmcIIIVarName | External Temperature Sensor.SetPtLowAlarm
InputRegister | ReadOnly | 2 | 1051 | 0x041B | 3 | reserved
InputRegister | ReadOnly | 2 | 1054 | 0x041E | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 1062 | 0x0426 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 1064 | 0x0428 | 2 | cmcIIIVarMax | 8000
InputRegister | ReadOnly | 2 | 1066 | 0x042A | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 1068 | 0x042C | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 1070 | 0x042E | 2 | reserved
InputRegister | ReadOnly | 2 | 1072 | 0x0430 | 2 | cmcIIIVarValueInt | External Temperature Sensor.Hysteresis 33
InputRegister | ReadOnly | 2 | 1074 | 0x0432 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1076 | 0x0434 | 1 | cmcIIIVarType | 6
InputRegister | ReadOnly | 2 | 1077 | 0x0435 | 32 | cmcIIIVarName | External Temperature Sensor.Hysteresis
InputRegister | ReadOnly | 2 | 1109 | 0x0455 | 3 | reserved
InputRegister | ReadOnly | 2 | 1112 | 0x0458 | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 2 | 1120 | 0x0460 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1122 | 0x0462 | 2 | cmcIIIVarMax | 2000
InputRegister | ReadOnly | 2 | 1124 | 0x0464 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 1126 | 0x0466 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 1128 | 0x0468 | 2 | reserved
InputRegister | ReadOnly | 2 | 1130 | 0x046A | 2 | cmcIIIVarValueInt | External Temperature Sensor.Category 36
InputRegister | ReadOnly | 2 | 1132 | 0x046C | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1134 | 0x046E | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1135 | 0x046F | 32 | cmcIIIVarName | External Temperature Sensor.Category
InputRegister | ReadOnly | 2 | 1167 | 0x048F | 3 | reserved
InputRegister | ReadOnly | 2 | 1170 | 0x0492 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1178 | 0x049A | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1180 | 0x049C | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1182 | 0x049E | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1184 | 0x04A0 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1186 | 0x04A2 | 2 | reserved
InputRegister | ReadOnly | 2 | 1188 | 0x04A4 | 2 | cmcIIIVarValueInt | Monitoring.Cooling.Category 47
InputRegister | ReadOnly | 2 | 1190 | 0x04A6 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1192 | 0x04A8 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1193 | 0x04A9 | 32 | cmcIIIVarName | Monitoring.Cooling.Category
InputRegister | ReadOnly | 2 | 1225 | 0x04C9 | 3 | reserved
InputRegister | ReadOnly | 2 | 1228 | 0x04CC | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1236 | 0x04D4 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1238 | 0x04D6 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1240 | 0x04D8 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1242 | 0x04DA | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1244 | 0x04DC | 2 | reserved
InputRegister | ReadOnly | 2 | 1246 | 0x04DE | 2 | cmcIIIVarValueInt | Monitoring.Internal Air Circuit.Category 52
InputRegister | ReadOnly | 2 | 1248 | 0x04E0 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1250 | 0x04E2 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1251 | 0x04E3 | 32 | cmcIIIVarName | Monitoring.Internal Air Circuit.Category
InputRegister | ReadOnly | 2 | 1283 | 0x0503 | 3 | reserved
InputRegister | ReadOnly | 2 | 1286 | 0x0506 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1294 | 0x050E | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1296 | 0x0510 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1298 | 0x0512 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1300 | 0x0514 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1302 | 0x0516 | 2 | reserved
InputRegister | ReadOnly | 2 | 1304 | 0x0518 | 2 | cmcIIIVarValueInt | Monitoring.External Air Circuit.Category 57
InputRegister | ReadOnly | 2 | 1306 | 0x051A | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1308 | 0x051C | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1309 | 0x051D | 32 | cmcIIIVarName | Monitoring.External Air Circuit.Category
InputRegister | ReadOnly | 2 | 1341 | 0x053D | 3 | reserved
InputRegister | ReadOnly | 2 | 1344 | 0x0540 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1352 | 0x0548 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1354 | 0x054A | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1356 | 0x054C | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1358 | 0x054E | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1360 | 0x0550 | 2 | reserved
InputRegister | ReadOnly | 2 | 1362 | 0x0552 | 2 | cmcIIIVarValueInt | Monitoring.Internal Fan.Category 63
InputRegister | ReadOnly | 2 | 1364 | 0x0554 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1366 | 0x0556 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1367 | 0x0557 | 32 | cmcIIIVarName | Monitoring.Internal Fan.Category
InputRegister | ReadOnly | 2 | 1399 | 0x0577 | 3 | reserved
InputRegister | ReadOnly | 2 | 1402 | 0x057A | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1410 | 0x0582 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1412 | 0x0584 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1414 | 0x0586 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1416 | 0x0588 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1418 | 0x058A | 2 | reserved
InputRegister | ReadOnly | 2 | 1420 | 0x058C | 2 | cmcIIIVarValueInt | Monitoring.External Fan.Category 69
InputRegister | ReadOnly | 2 | 1422 | 0x058E | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1424 | 0x0590 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1425 | 0x0591 | 32 | cmcIIIVarName | Monitoring.External Fan.Category
InputRegister | ReadOnly | 2 | 1457 | 0x05B1 | 3 | reserved
InputRegister | ReadOnly | 2 | 1460 | 0x05B4 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1468 | 0x05BC | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1470 | 0x05BE | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1472 | 0x05C0 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1474 | 0x05C2 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1476 | 0x05C4 | 2 | reserved
InputRegister | ReadOnly | 2 | 1478 | 0x05C6 | 2 | cmcIIIVarValueInt | Monitoring.Compressor.Category 75
InputRegister | ReadOnly | 2 | 1480 | 0x05C8 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1482 | 0x05CA | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1483 | 0x05CB | 32 | cmcIIIVarName | Monitoring.Compressor.Category
InputRegister | ReadOnly | 2 | 1515 | 0x05EB | 3 | reserved
InputRegister | ReadOnly | 2 | 1518 | 0x05EE | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1526 | 0x05F6 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1528 | 0x05F8 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1530 | 0x05FA | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1532 | 0x05FC | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1534 | 0x05FE | 2 | reserved
InputRegister | ReadOnly | 2 | 1536 | 0x0600 | 2 | cmcIIIVarValueInt | Monitoring.EEV.Category 81
InputRegister | ReadOnly | 2 | 1538 | 0x0602 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1540 | 0x0604 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1541 | 0x0605 | 32 | cmcIIIVarName | Monitoring.EEV.Category
InputRegister | ReadOnly | 2 | 1573 | 0x0625 | 3 | reserved
InputRegister | ReadOnly | 2 | 1576 | 0x0628 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1584 | 0x0630 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1586 | 0x0632 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1588 | 0x0634 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1590 | 0x0636 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1592 | 0x0638 | 2 | reserved
InputRegister | ReadOnly | 2 | 1594 | 0x063A | 2 | cmcIIIVarValueInt | Monitoring.Filter.Category 85
InputRegister | ReadOnly | 2 | 1596 | 0x063C | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1598 | 0x063E | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1599 | 0x063F | 32 | cmcIIIVarName | Monitoring.Filter.Category
InputRegister | ReadOnly | 2 | 1631 | 0x065F | 3 | reserved
InputRegister | ReadOnly | 2 | 1634 | 0x0662 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1642 | 0x066A | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1644 | 0x066C | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1646 | 0x066E | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1648 | 0x0670 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1650 | 0x0672 | 2 | reserved
InputRegister | ReadOnly | 2 | 1652 | 0x0674 | 2 | cmcIIIVarValueInt | Monitoring.Door.Category 89
InputRegister | ReadOnly | 2 | 1654 | 0x0676 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1656 | 0x0678 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1657 | 0x0679 | 32 | cmcIIIVarName | Monitoring.Door.Category
InputRegister | ReadOnly | 2 | 1689 | 0x0699 | 3 | reserved
InputRegister | ReadOnly | 2 | 1692 | 0x069C | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1700 | 0x06A4 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1702 | 0x06A6 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1704 | 0x06A8 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1706 | 0x06AA | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1708 | 0x06AC | 2 | reserved
InputRegister | ReadOnly | 2 | 1710 | 0x06AE | 2 | cmcIIIVarValueInt | Monitoring.Electronics.Category 93
InputRegister | ReadOnly | 2 | 1712 | 0x06B0 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1714 | 0x06B2 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1715 | 0x06B3 | 32 | cmcIIIVarName | Monitoring.Electronics.Category
InputRegister | ReadOnly | 2 | 1747 | 0x06D3 | 3 | reserved
InputRegister | ReadOnly | 2 | 1750 | 0x06D6 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1758 | 0x06DE | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1760 | 0x06E0 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1762 | 0x06E2 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1764 | 0x06E4 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1766 | 0x06E6 | 2 | reserved
InputRegister | ReadOnly | 2 | 1768 | 0x06E8 | 2 | cmcIIIVarValueInt | Monitoring.Condensate.Category 97
InputRegister | ReadOnly | 2 | 1770 | 0x06EA | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1772 | 0x06EC | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1773 | 0x06ED | 32 | cmcIIIVarName | Monitoring.Condensate.Category
InputRegister | ReadOnly | 2 | 1805 | 0x070D | 3 | reserved
InputRegister | ReadOnly | 2 | 1808 | 0x0710 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1816 | 0x0718 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1818 | 0x071A | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1820 | 0x071C | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1822 | 0x071E | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1824 | 0x0720 | 2 | reserved
InputRegister | ReadOnly | 2 | 1826 | 0x0722 | 2 | cmcIIIVarValueInt | Monitoring.System Messages.Category 101
InputRegister | ReadOnly | 2 | 1828 | 0x0724 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1830 | 0x0726 | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 1831 | 0x0727 | 32 | cmcIIIVarName | Monitoring.System Messages.Category
InputRegister | ReadOnly | 2 | 1863 | 0x0747 | 3 | reserved
InputRegister | ReadOnly | 2 | 1866 | 0x074A | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 1874 | 0x0752 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 1876 | 0x0754 | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 1878 | 0x0756 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 1880 | 0x0758 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 1882 | 0x075A | 2 | reserved
InputRegister | ReadOnly | 2 | 1884 | 0x075C | 2 | cmcIIIVarValueInt | Setup.Mode 115
InputRegister | ReadOnly | 2 | 1886 | 0x075E | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1888 | 0x0760 | 1 | cmcIIIVarType | 126
InputRegister | ReadOnly | 2 | 1889 | 0x0761 | 32 | cmcIIIVarName | Setup.Mode
InputRegister | ReadOnly | 2 | 1921 | 0x0781 | 32 | cmcIIIVarConstraints | 0,1,2
InputRegister | ReadOnly | 2 | 1953 | 0x07A1 | 2 | reserved
InputRegister | ReadOnly | 2 | 1955 | 0x07A3 | 2 | cmcIIIVarValueInt | Setup.Alarm Tolerance Filter 116
InputRegister | ReadOnly | 2 | 1957 | 0x07A5 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 1959 | 0x07A7 | 1 | cmcIIIVarType | 17
InputRegister | ReadOnly | 2 | 1960 | 0x07A8 | 32 | cmcIIIVarName | Setup.Alarm Tolerance Filter
InputRegister | ReadOnly | 2 | 1992 | 0x07C8 | 3 | reserved
InputRegister | ReadOnly | 2 | 1995 | 0x07CB | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 2003 | 0x07D3 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 2005 | 0x07D5 | 2 | cmcIIIVarMax | 5
InputRegister | ReadOnly | 2 | 2007 | 0x07D7 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 2009 | 0x07D9 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 2011 | 0x07DB | 2 | reserved
InputRegister | ReadOnly | 2 | 2013 | 0x07DD | 2 | cmcIIIVarValueInt | Setup.Standard Control.Setpoint 117
InputRegister | ReadOnly | 2 | 2015 | 0x07DF | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2017 | 0x07E1 | 1 | cmcIIIVarType | 17
InputRegister | ReadOnly | 2 | 2018 | 0x07E2 | 32 | cmcIIIVarName | Setup.Standard Control.Setpoint
InputRegister | ReadOnly | 2 | 2050 | 0x0802 | 3 | reserved
InputRegister | ReadOnly | 2 | 2053 | 0x0805 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 2061 | 0x080D | 2 | cmcIIIVarMin | 2000
InputRegister | ReadOnly | 2 | 2063 | 0x080F | 2 | cmcIIIVarMax | 5000
InputRegister | ReadOnly | 2 | 2065 | 0x0811 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 2067 | 0x0813 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 2069 | 0x0815 | 2 | reserved
InputRegister | ReadOnly | 2 | 2071 | 0x0817 | 2 | cmcIIIVarValueInt | Setup.Standard Control.Alarm Threshold 118
InputRegister | ReadOnly | 2 | 2073 | 0x0819 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2075 | 0x081B | 1 | cmcIIIVarType | 17
InputRegister | ReadOnly | 2 | 2076 | 0x081C | 32 | cmcIIIVarName | Setup.Standard Control.Alarm Threshold
InputRegister | ReadOnly | 2 | 2108 | 0x083C | 3 | reserved
InputRegister | ReadOnly | 2 | 2111 | 0x083F | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 2119 | 0x0847 | 2 | cmcIIIVarMin | 300
InputRegister | ReadOnly | 2 | 2121 | 0x0849 | 2 | cmcIIIVarMax | 1500
InputRegister | ReadOnly | 2 | 2123 | 0x084B | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 2125 | 0x084D | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 2127 | 0x084F | 2 | reserved
InputRegister | ReadOnly | 2 | 2129 | 0x0851 | 2 | cmcIIIVarValueInt | Setup.Outlet Temperature.Setpoint 119
InputRegister | ReadOnly | 2 | 2131 | 0x0853 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2133 | 0x0855 | 1 | cmcIIIVarType | 17
InputRegister | ReadOnly | 2 | 2134 | 0x0856 | 32 | cmcIIIVarName | Setup.Outlet Temperature.Setpoint
InputRegister | ReadOnly | 2 | 2166 | 0x0876 | 3 | reserved
InputRegister | ReadOnly | 2 | 2169 | 0x0879 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 2177 | 0x0881 | 2 | cmcIIIVarMin | 1800
InputRegister | ReadOnly | 2 | 2179 | 0x0883 | 2 | cmcIIIVarMax | 2800
InputRegister | ReadOnly | 2 | 2181 | 0x0885 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 2183 | 0x0887 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 2185 | 0x0889 | 2 | reserved
InputRegister | ReadOnly | 2 | 2187 | 0x088B | 2 | cmcIIIVarValueInt | Setup.Outlet Temperature.Alarm Threshold 120
InputRegister | ReadOnly | 2 | 2189 | 0x088D | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2191 | 0x088F | 1 | cmcIIIVarType | 17
InputRegister | ReadOnly | 2 | 2192 | 0x0890 | 32 | cmcIIIVarName | Setup.Outlet Temperature.Alarm Threshold
InputRegister | ReadOnly | 2 | 2224 | 0x08B0 | 3 | reserved
InputRegister | ReadOnly | 2 | 2227 | 0x08B3 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 2235 | 0x08BB | 2 | cmcIIIVarMin | 1200
InputRegister | ReadOnly | 2 | 2237 | 0x08BD | 2 | cmcIIIVarMax | 2400
InputRegister | ReadOnly | 2 | 2239 | 0x08BF | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 2241 | 0x08C1 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 2243 | 0x08C3 | 2 | reserved
InputRegister | ReadOnly | 2 | 2245 | 0x08C5 | 2 | cmcIIIVarValueInt | Information.Class 0
InputRegister | ReadOnly | 2 | 2247 | 0x08C7 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2249 | 0x08C9 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 2250 | 0x08CA | 32 | cmcIIIVarName | Information.Class
InputRegister | ReadOnly | 2 | 2282 | 0x08EA | 3 | reserved
InputRegister | ReadOnly | 2 | 2285 | 0x08ED | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 2293 | 0x08F5 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 2295 | 0x08F7 | 2 | cmcIIIVarMax | 65535
InputRegister | ReadOnly | 2 | 2297 | 0x08F9 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 2299 | 0x08FB | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 2301 | 0x08FD | 2 | reserved
InputRegister | ReadOnly | 2 | 2303 | 0x08FF | 2 | cmcIIIVarValueInt | Information.Product Family 1
InputRegister | ReadOnly | 2 | 2305 | 0x0901 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2307 | 0x0903 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 2308 | 0x0904 | 32 | cmcIIIVarName | Information.Product Family
InputRegister | ReadOnly | 2 | 2340 | 0x0924 | 3 | reserved
InputRegister | ReadOnly | 2 | 2343 | 0x0927 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 2351 | 0x092F | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 2353 | 0x0931 | 2 | cmcIIIVarMax | 65535
InputRegister | ReadOnly | 2 | 2355 | 0x0933 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 2357 | 0x0935 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 2359 | 0x0937 | 2 | reserved
InputRegister | ReadOnly | 2 | 2361 | 0x0939 | 2 | cmcIIIVarValueInt | Information.BOM Version 2
InputRegister | ReadOnly | 2 | 2363 | 0x093B | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2365 | 0x093D | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 2366 | 0x093E | 32 | cmcIIIVarName | Information.BOM Version
InputRegister | ReadOnly | 2 | 2398 | 0x095E | 3 | reserved
InputRegister | ReadOnly | 2 | 2401 | 0x0961 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 2409 | 0x0969 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 2411 | 0x096B | 2 | cmcIIIVarMax | 2147483647
InputRegister | ReadOnly | 2 | 2413 | 0x096D | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 2415 | 0x096F | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 2417 | 0x0971 | 2 | reserved
InputRegister | ReadOnly | 2 | 2419 | 0x0973 | 2 | cmcIIIVarValueInt | Information.Device Operating Time 6
InputRegister | ReadOnly | 2 | 2421 | 0x0975 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2423 | 0x0977 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 2424 | 0x0978 | 32 | cmcIIIVarName | Information.Device Operating Time
InputRegister | ReadOnly | 2 | 2456 | 0x0998 | 3 | reserved
InputRegister | ReadOnly | 2 | 2459 | 0x099B | 8 | cmcIIIVarUnit | h
InputRegister | ReadOnly | 2 | 2467 | 0x09A3 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 2469 | 0x09A5 | 2 | cmcIIIVarMax | 999999999
InputRegister | ReadOnly | 2 | 2471 | 0x09A7 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 2473 | 0x09A9 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 2475 | 0x09AB | 2 | reserved
InputRegister | ReadOnly | 2 | 2477 | 0x09AD | 2 | cmcIIIVarValueInt | Internal Temperature.Value 8
InputRegister | ReadOnly | 2 | 2479 | 0x09AF | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2481 | 0x09B1 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 2482 | 0x09B2 | 32 | cmcIIIVarName | Internal Temperature.Value
InputRegister | ReadOnly | 2 | 2514 | 0x09D2 | 3 | reserved
InputRegister | ReadOnly | 2 | 2517 | 0x09D5 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 2525 | 0x09DD | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 2527 | 0x09DF | 2 | cmcIIIVarMax | 9000
InputRegister | ReadOnly | 2 | 2529 | 0x09E1 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 2531 | 0x09E3 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 2533 | 0x09E5 | 2 | reserved
InputRegister | ReadOnly | 2 | 2535 | 0x09E7 | 2 | cmcIIIVarValueInt | Internal Temperature.Status 15
InputRegister | ReadOnly | 2 | 2537 | 0x09E9 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2539 | 0x09EB | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 2540 | 0x09EC | 32 | cmcIIIVarName | Internal Temperature.Status
InputRegister | ReadOnly | 2 | 2572 | 0x0A0C | 32 | cmcIIIVarConstraints | 1,3,4,5,6,7,8,9
InputRegister | ReadOnly | 2 | 2604 | 0x0A2C | 2 | reserved
InputRegister | ReadOnly | 2 | 2606 | 0x0A2E | 2 | cmcIIIVarValueInt | Ambient Temperature.Value 18
InputRegister | ReadOnly | 2 | 2608 | 0x0A30 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2610 | 0x0A32 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 2611 | 0x0A33 | 32 | cmcIIIVarName | Ambient Temperature.Value
InputRegister | ReadOnly | 2 | 2643 | 0x0A53 | 3 | reserved
InputRegister | ReadOnly | 2 | 2646 | 0x0A56 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 2654 | 0x0A5E | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 2656 | 0x0A60 | 2 | cmcIIIVarMax | 9000
InputRegister | ReadOnly | 2 | 2658 | 0x0A62 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 2660 | 0x0A64 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 2662 | 0x0A66 | 2 | reserved
InputRegister | ReadOnly | 2 | 2664 | 0x0A68 | 2 | cmcIIIVarValueInt | Ambient Temperature.Status 25
InputRegister | ReadOnly | 2 | 2666 | 0x0A6A | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2668 | 0x0A6C | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 2669 | 0x0A6D | 32 | cmcIIIVarName | Ambient Temperature.Status
InputRegister | ReadOnly | 2 | 2701 | 0x0A8D | 32 | cmcIIIVarConstraints | 1,3,4,6,7,8,9,33
InputRegister | ReadOnly | 2 | 2733 | 0x0AAD | 2 | reserved
InputRegister | ReadOnly | 2 | 2735 | 0x0AAF | 2 | cmcIIIVarValueInt | External Temperature Sensor.Value 28
InputRegister | ReadOnly | 2 | 2737 | 0x0AB1 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2739 | 0x0AB3 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 2740 | 0x0AB4 | 32 | cmcIIIVarName | External Temperature Sensor.Value
InputRegister | ReadOnly | 2 | 2772 | 0x0AD4 | 3 | reserved
InputRegister | ReadOnly | 2 | 2775 | 0x0AD7 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 2783 | 0x0ADF | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 2785 | 0x0AE1 | 2 | cmcIIIVarMax | 9000
InputRegister | ReadOnly | 2 | 2787 | 0x0AE3 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 2789 | 0x0AE5 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 2791 | 0x0AE7 | 2 | reserved
InputRegister | ReadOnly | 2 | 2793 | 0x0AE9 | 2 | cmcIIIVarValueInt | External Temperature Sensor.Status 35
InputRegister | ReadOnly | 2 | 2795 | 0x0AEB | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2797 | 0x0AED | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 2798 | 0x0AEE | 32 | cmcIIIVarName | External Temperature Sensor.Status
InputRegister | ReadOnly | 2 | 2830 | 0x0B0E | 32 | cmcIIIVarConstraints | 1,3,4,6,7,8,9
InputRegister | ReadOnly | 2 | 2862 | 0x0B2E | 2 | reserved
InputRegister | ReadOnly | 2 | 2864 | 0x0B30 | 2 | cmcIIIVarValueInt | Monitoring.Cooling.Operating Mode 38
InputRegister | ReadOnly | 2 | 2866 | 0x0B32 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2868 | 0x0B34 | 1 | cmcIIIVarType | 145
InputRegister | ReadOnly | 2 | 2869 | 0x0B35 | 32 | cmcIIIVarName | Monitoring.Cooling.Operating Mode
InputRegister | ReadOnly | 2 | 2901 | 0x0B55 | 32 | cmcIIIVarConstraints | 0,1,2,3
InputRegister | ReadOnly | 2 | 2933 | 0x0B75 | 2 | reserved
InputRegister | ReadOnly | 2 | 2935 | 0x0B77 | 2 | cmcIIIVarValueInt | Monitoring.Cooling.Selftest Progress 40
InputRegister | ReadOnly | 2 | 2937 | 0x0B79 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2939 | 0x0B7B | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 2940 | 0x0B7C | 32 | cmcIIIVarName | Monitoring.Cooling.Selftest Progress
InputRegister | ReadOnly | 2 | 2972 | 0x0B9C | 3 | reserved
InputRegister | ReadOnly | 2 | 2975 | 0x0B9F | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 2 | 2983 | 0x0BA7 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 2985 | 0x0BA9 | 2 | cmcIIIVarMax | 100
InputRegister | ReadOnly | 2 | 2987 | 0x0BAB | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 2989 | 0x0BAD | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 2991 | 0x0BAF | 2 | reserved
InputRegister | ReadOnly | 2 | 2993 | 0x0BB1 | 2 | cmcIIIVarValueInt | Monitoring.Cooling.Capacity 41
InputRegister | ReadOnly | 2 | 2995 | 0x0BB3 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 2997 | 0x0BB5 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 2998 | 0x0BB6 | 32 | cmcIIIVarName | Monitoring.Cooling.Capacity
InputRegister | ReadOnly | 2 | 3030 | 0x0BD6 | 3 | reserved
InputRegister | ReadOnly | 2 | 3033 | 0x0BD9 | 8 | cmcIIIVarUnit | W
InputRegister | ReadOnly | 2 | 3041 | 0x0BE1 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 3043 | 0x0BE3 | 2 | cmcIIIVarMax | 10000
InputRegister | ReadOnly | 2 | 3045 | 0x0BE5 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 3047 | 0x0BE7 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 3049 | 0x0BE9 | 2 | reserved
InputRegister | ReadOnly | 2 | 3051 | 0x0BEB | 2 | cmcIIIVarValueInt | Monitoring.Cooling.Cooling Capacity 42
InputRegister | ReadOnly | 2 | 3053 | 0x0BED | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3055 | 0x0BEF | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3056 | 0x0BF0 | 32 | cmcIIIVarName | Monitoring.Cooling.Cooling Capacity
InputRegister | ReadOnly | 2 | 3088 | 0x0C10 | 3 | reserved
InputRegister | ReadOnly | 2 | 3091 | 0x0C13 | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 2 | 3099 | 0x0C1B | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 3101 | 0x0C1D | 2 | cmcIIIVarMax | 100
InputRegister | ReadOnly | 2 | 3103 | 0x0C1F | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 3105 | 0x0C21 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 3107 | 0x0C23 | 2 | reserved
InputRegister | ReadOnly | 2 | 3109 | 0x0C25 | 2 | cmcIIIVarValueInt | Monitoring.Cooling.EER 43
InputRegister | ReadOnly | 2 | 3111 | 0x0C27 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3113 | 0x0C29 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3114 | 0x0C2A | 32 | cmcIIIVarName | Monitoring.Cooling.EER
InputRegister | ReadOnly | 2 | 3146 | 0x0C4A | 3 | reserved
InputRegister | ReadOnly | 2 | 3149 | 0x0C4D | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 3157 | 0x0C55 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 3159 | 0x0C57 | 2 | cmcIIIVarMax | 10000
InputRegister | ReadOnly | 2 | 3161 | 0x0C59 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 3163 | 0x0C5B | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 3165 | 0x0C5D | 2 | reserved
InputRegister | ReadOnly | 2 | 3167 | 0x0C5F | 2 | cmcIIIVarValueInt | Monitoring.Cooling.EER 24h 44
InputRegister | ReadOnly | 2 | 3169 | 0x0C61 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3171 | 0x0C63 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3172 | 0x0C64 | 32 | cmcIIIVarName | Monitoring.Cooling.EER 24h
InputRegister | ReadOnly | 2 | 3204 | 0x0C84 | 3 | reserved
InputRegister | ReadOnly | 2 | 3207 | 0x0C87 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 3215 | 0x0C8F | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 3217 | 0x0C91 | 2 | cmcIIIVarMax | 10000
InputRegister | ReadOnly | 2 | 3219 | 0x0C93 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 3221 | 0x0C95 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 3223 | 0x0C97 | 2 | reserved
InputRegister | ReadOnly | 2 | 3225 | 0x0C99 | 2 | cmcIIIVarValueInt | Monitoring.Cooling.Status 46
InputRegister | ReadOnly | 2 | 3227 | 0x0C9B | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3229 | 0x0C9D | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 3230 | 0x0C9E | 32 | cmcIIIVarName | Monitoring.Cooling.Status
InputRegister | ReadOnly | 2 | 3262 | 0x0CBE | 32 | cmcIIIVarConstraints | 1,4,5
InputRegister | ReadOnly | 2 | 3294 | 0x0CDE | 2 | reserved
InputRegister | ReadOnly | 2 | 3296 | 0x0CE0 | 2 | cmcIIIVarValueInt | Monitoring.Internal Air Circuit.Value 49
InputRegister | ReadOnly | 2 | 3298 | 0x0CE2 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3300 | 0x0CE4 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3301 | 0x0CE5 | 32 | cmcIIIVarName | Monitoring.Internal Air Circuit.Value
InputRegister | ReadOnly | 2 | 3333 | 0x0D05 | 3 | reserved
InputRegister | ReadOnly | 2 | 3336 | 0x0D08 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 3344 | 0x0D10 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 3346 | 0x0D12 | 2 | cmcIIIVarMax | 9000
InputRegister | ReadOnly | 2 | 3348 | 0x0D14 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 3350 | 0x0D16 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 3352 | 0x0D18 | 2 | reserved
InputRegister | ReadOnly | 2 | 3354 | 0x0D1A | 2 | cmcIIIVarValueInt | Monitoring.Internal Air Circuit.Status 51
InputRegister | ReadOnly | 2 | 3356 | 0x0D1C | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3358 | 0x0D1E | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 3359 | 0x0D1F | 32 | cmcIIIVarName | Monitoring.Internal Air Circuit.Status
InputRegister | ReadOnly | 2 | 3391 | 0x0D3F | 32 | cmcIIIVarConstraints | 1,4,7
InputRegister | ReadOnly | 2 | 3423 | 0x0D5F | 2 | reserved
InputRegister | ReadOnly | 2 | 3425 | 0x0D61 | 2 | cmcIIIVarValueInt | Monitoring.External Air Circuit.Value 54
InputRegister | ReadOnly | 2 | 3427 | 0x0D63 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3429 | 0x0D65 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3430 | 0x0D66 | 32 | cmcIIIVarName | Monitoring.External Air Circuit.Value
InputRegister | ReadOnly | 2 | 3462 | 0x0D86 | 3 | reserved
InputRegister | ReadOnly | 2 | 3465 | 0x0D89 | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 3473 | 0x0D91 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 3475 | 0x0D93 | 2 | cmcIIIVarMax | 9000
InputRegister | ReadOnly | 2 | 3477 | 0x0D95 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 3479 | 0x0D97 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 3481 | 0x0D99 | 2 | reserved
InputRegister | ReadOnly | 2 | 3483 | 0x0D9B | 2 | cmcIIIVarValueInt | Monitoring.External Air Circuit.Status 56
InputRegister | ReadOnly | 2 | 3485 | 0x0D9D | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3487 | 0x0D9F | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 3488 | 0x0DA0 | 32 | cmcIIIVarName | Monitoring.External Air Circuit.Status
InputRegister | ReadOnly | 2 | 3520 | 0x0DC0 | 32 | cmcIIIVarConstraints | 1,4,8
InputRegister | ReadOnly | 2 | 3552 | 0x0DE0 | 2 | reserved
InputRegister | ReadOnly | 2 | 3554 | 0x0DE2 | 2 | cmcIIIVarValueInt | Monitoring.Internal Fan.Value 59
InputRegister | ReadOnly | 2 | 3556 | 0x0DE4 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3558 | 0x0DE6 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3559 | 0x0DE7 | 32 | cmcIIIVarName | Monitoring.Internal Fan.Value
InputRegister | ReadOnly | 2 | 3591 | 0x0E07 | 3 | reserved
InputRegister | ReadOnly | 2 | 3594 | 0x0E0A | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 2 | 3602 | 0x0E12 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 3604 | 0x0E14 | 2 | cmcIIIVarMax | 100
InputRegister | ReadOnly | 2 | 3606 | 0x0E16 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 3608 | 0x0E18 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 3610 | 0x0E1A | 2 | reserved
InputRegister | ReadOnly | 2 | 3612 | 0x0E1C | 2 | cmcIIIVarValueInt | Monitoring.Internal Fan.Operating Time 60
InputRegister | ReadOnly | 2 | 3614 | 0x0E1E | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3616 | 0x0E20 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3617 | 0x0E21 | 32 | cmcIIIVarName | Monitoring.Internal Fan.Operating Time
InputRegister | ReadOnly | 2 | 3649 | 0x0E41 | 3 | reserved
InputRegister | ReadOnly | 2 | 3652 | 0x0E44 | 8 | cmcIIIVarUnit | h
InputRegister | ReadOnly | 2 | 3660 | 0x0E4C | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 3662 | 0x0E4E | 2 | cmcIIIVarMax | 999999999
InputRegister | ReadOnly | 2 | 3664 | 0x0E50 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 3666 | 0x0E52 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 3668 | 0x0E54 | 2 | reserved
InputRegister | ReadOnly | 2 | 3670 | 0x0E56 | 2 | cmcIIIVarValueInt | Monitoring.Internal Fan.Status 62
InputRegister | ReadOnly | 2 | 3672 | 0x0E58 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3674 | 0x0E5A | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 3675 | 0x0E5B | 32 | cmcIIIVarName | Monitoring.Internal Fan.Status
InputRegister | ReadOnly | 2 | 3707 | 0x0E7B | 32 | cmcIIIVarConstraints | 1,4,7,9
InputRegister | ReadOnly | 2 | 3739 | 0x0E9B | 2 | reserved
InputRegister | ReadOnly | 2 | 3741 | 0x0E9D | 2 | cmcIIIVarValueInt | Monitoring.External Fan.Value 65
InputRegister | ReadOnly | 2 | 3743 | 0x0E9F | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3745 | 0x0EA1 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3746 | 0x0EA2 | 32 | cmcIIIVarName | Monitoring.External Fan.Value
InputRegister | ReadOnly | 2 | 3778 | 0x0EC2 | 3 | reserved
InputRegister | ReadOnly | 2 | 3781 | 0x0EC5 | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 2 | 3789 | 0x0ECD | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 3791 | 0x0ECF | 2 | cmcIIIVarMax | 100
InputRegister | ReadOnly | 2 | 3793 | 0x0ED1 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 3795 | 0x0ED3 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 3797 | 0x0ED5 | 2 | reserved
InputRegister | ReadOnly | 2 | 3799 | 0x0ED7 | 2 | cmcIIIVarValueInt | Monitoring.External Fan.Operating Time 66
InputRegister | ReadOnly | 2 | 3801 | 0x0ED9 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3803 | 0x0EDB | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3804 | 0x0EDC | 32 | cmcIIIVarName | Monitoring.External Fan.Operating Time
InputRegister | ReadOnly | 2 | 3836 | 0x0EFC | 3 | reserved
InputRegister | ReadOnly | 2 | 3839 | 0x0EFF | 8 | cmcIIIVarUnit | h
InputRegister | ReadOnly | 2 | 3847 | 0x0F07 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 3849 | 0x0F09 | 2 | cmcIIIVarMax | 999999999
InputRegister | ReadOnly | 2 | 3851 | 0x0F0B | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 3853 | 0x0F0D | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 3855 | 0x0F0F | 2 | reserved
InputRegister | ReadOnly | 2 | 3857 | 0x0F11 | 2 | cmcIIIVarValueInt | Monitoring.External Fan.Status 68
InputRegister | ReadOnly | 2 | 3859 | 0x0F13 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3861 | 0x0F15 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 3862 | 0x0F16 | 32 | cmcIIIVarName | Monitoring.External Fan.Status
InputRegister | ReadOnly | 2 | 3894 | 0x0F36 | 32 | cmcIIIVarConstraints | 1,4,7,9
InputRegister | ReadOnly | 2 | 3926 | 0x0F56 | 2 | reserved
InputRegister | ReadOnly | 2 | 3928 | 0x0F58 | 2 | cmcIIIVarValueInt | Monitoring.Compressor.Speed 71
InputRegister | ReadOnly | 2 | 3930 | 0x0F5A | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3932 | 0x0F5C | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3933 | 0x0F5D | 32 | cmcIIIVarName | Monitoring.Compressor.Speed
InputRegister | ReadOnly | 2 | 3965 | 0x0F7D | 3 | reserved
InputRegister | ReadOnly | 2 | 3968 | 0x0F80 | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 2 | 3976 | 0x0F88 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 3978 | 0x0F8A | 2 | cmcIIIVarMax | 100
InputRegister | ReadOnly | 2 | 3980 | 0x0F8C | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 3982 | 0x0F8E | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 3984 | 0x0F90 | 2 | reserved
InputRegister | ReadOnly | 2 | 3986 | 0x0F92 | 2 | cmcIIIVarValueInt | Monitoring.Compressor.Operating Time 72
InputRegister | ReadOnly | 2 | 3988 | 0x0F94 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 3990 | 0x0F96 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 3991 | 0x0F97 | 32 | cmcIIIVarName | Monitoring.Compressor.Operating Time
InputRegister | ReadOnly | 2 | 4023 | 0x0FB7 | 3 | reserved
InputRegister | ReadOnly | 2 | 4026 | 0x0FBA | 8 | cmcIIIVarUnit | h
InputRegister | ReadOnly | 2 | 4034 | 0x0FC2 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 4036 | 0x0FC4 | 2 | cmcIIIVarMax | 999999999
InputRegister | ReadOnly | 2 | 4038 | 0x0FC6 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 4040 | 0x0FC8 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 4042 | 0x0FCA | 2 | reserved
InputRegister | ReadOnly | 2 | 4044 | 0x0FCC | 2 | cmcIIIVarValueInt | Monitoring.Compressor.Status 74
InputRegister | ReadOnly | 2 | 4046 | 0x0FCE | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4048 | 0x0FD0 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 4049 | 0x0FD1 | 32 | cmcIIIVarName | Monitoring.Compressor.Status
InputRegister | ReadOnly | 2 | 4081 | 0x0FF1 | 32 | cmcIIIVarConstraints | 1,3,4
InputRegister | ReadOnly | 2 | 4113 | 0x1011 | 2 | reserved
InputRegister | ReadOnly | 2 | 4115 | 0x1013 | 2 | cmcIIIVarValueInt | Monitoring.EEV.Value 77
InputRegister | ReadOnly | 2 | 4117 | 0x1015 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4119 | 0x1017 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 4120 | 0x1018 | 32 | cmcIIIVarName | Monitoring.EEV.Value
InputRegister | ReadOnly | 2 | 4152 | 0x1038 | 3 | reserved
InputRegister | ReadOnly | 2 | 4155 | 0x103B | 8 | cmcIIIVarUnit | 캜
InputRegister | ReadOnly | 2 | 4163 | 0x1043 | 2 | cmcIIIVarMin | -3000
InputRegister | ReadOnly | 2 | 4165 | 0x1045 | 2 | cmcIIIVarMax | 9000
InputRegister | ReadOnly | 2 | 4167 | 0x1047 | 2 | cmcIIIVarScale | 10
InputRegister | ReadOnly | 2 | 4169 | 0x1049 | 2 | cmcIIIVarSteps | 10
InputRegister | ReadOnly | 2 | 4171 | 0x104B | 2 | reserved
InputRegister | ReadOnly | 2 | 4173 | 0x104D | 2 | cmcIIIVarValueInt | Monitoring.EEV.Position 78
InputRegister | ReadOnly | 2 | 4175 | 0x104F | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4177 | 0x1051 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 4178 | 0x1052 | 32 | cmcIIIVarName | Monitoring.EEV.Position
InputRegister | ReadOnly | 2 | 4210 | 0x1072 | 3 | reserved
InputRegister | ReadOnly | 2 | 4213 | 0x1075 | 8 | cmcIIIVarUnit | %
InputRegister | ReadOnly | 2 | 4221 | 0x107D | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 4223 | 0x107F | 2 | cmcIIIVarMax | 100
InputRegister | ReadOnly | 2 | 4225 | 0x1081 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 4227 | 0x1083 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 4229 | 0x1085 | 2 | reserved
InputRegister | ReadOnly | 2 | 4231 | 0x1087 | 2 | cmcIIIVarValueInt | Monitoring.EEV.Status 80
InputRegister | ReadOnly | 2 | 4233 | 0x1089 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4235 | 0x108B | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 4236 | 0x108C | 32 | cmcIIIVarName | Monitoring.EEV.Status
InputRegister | ReadOnly | 2 | 4268 | 0x10AC | 32 | cmcIIIVarConstraints | 1,3,4
InputRegister | ReadOnly | 2 | 4300 | 0x10CC | 2 | reserved
InputRegister | ReadOnly | 2 | 4302 | 0x10CE | 2 | cmcIIIVarValueInt | Monitoring.Filter.Status 84
InputRegister | ReadOnly | 2 | 4304 | 0x10D0 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4306 | 0x10D2 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 4307 | 0x10D3 | 32 | cmcIIIVarName | Monitoring.Filter.Status
InputRegister | ReadOnly | 2 | 4339 | 0x10F3 | 32 | cmcIIIVarConstraints | 1,4,33
InputRegister | ReadOnly | 2 | 4371 | 0x1113 | 2 | reserved
InputRegister | ReadOnly | 2 | 4373 | 0x1115 | 2 | cmcIIIVarValueInt | Monitoring.Door.Status 88
InputRegister | ReadOnly | 2 | 4375 | 0x1117 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4377 | 0x1119 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 4378 | 0x111A | 32 | cmcIIIVarName | Monitoring.Door.Status
InputRegister | ReadOnly | 2 | 4410 | 0x113A | 32 | cmcIIIVarConstraints | 4,12,13
InputRegister | ReadOnly | 2 | 4442 | 0x115A | 2 | reserved
InputRegister | ReadOnly | 2 | 4444 | 0x115C | 2 | cmcIIIVarValueInt | Monitoring.Electronics.Status 92
InputRegister | ReadOnly | 2 | 4446 | 0x115E | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4448 | 0x1160 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 4449 | 0x1161 | 32 | cmcIIIVarName | Monitoring.Electronics.Status
InputRegister | ReadOnly | 2 | 4481 | 0x1181 | 32 | cmcIIIVarConstraints | 1,3,4,5
InputRegister | ReadOnly | 2 | 4513 | 0x11A1 | 2 | reserved
InputRegister | ReadOnly | 2 | 4515 | 0x11A3 | 2 | cmcIIIVarValueInt | Monitoring.Condensate.Status 96
InputRegister | ReadOnly | 2 | 4517 | 0x11A5 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4519 | 0x11A7 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 4520 | 0x11A8 | 32 | cmcIIIVarName | Monitoring.Condensate.Status
InputRegister | ReadOnly | 2 | 4552 | 0x11C8 | 32 | cmcIIIVarConstraints | 1,4,33
InputRegister | ReadOnly | 2 | 4584 | 0x11E8 | 2 | reserved
InputRegister | ReadOnly | 2 | 4586 | 0x11EA | 2 | cmcIIIVarValueInt | Monitoring.System Messages.Status 100
InputRegister | ReadOnly | 2 | 4588 | 0x11EC | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4590 | 0x11EE | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 4591 | 0x11EF | 32 | cmcIIIVarName | Monitoring.System Messages.Status
InputRegister | ReadOnly | 2 | 4623 | 0x120F | 32 | cmcIIIVarConstraints | 1,4,5,33
InputRegister | ReadOnly | 2 | 4655 | 0x122F | 2 | reserved
InputRegister | ReadOnly | 2 | 4657 | 0x1231 | 2 | cmcIIIVarValueInt | Monitoring.Error List.Error 1 103
InputRegister | ReadOnly | 2 | 4659 | 0x1233 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4661 | 0x1235 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 4662 | 0x1236 | 32 | cmcIIIVarName | Monitoring.Error List.Error 1
InputRegister | ReadOnly | 2 | 4694 | 0x1256 | 3 | reserved
InputRegister | ReadOnly | 2 | 4697 | 0x1259 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 4705 | 0x1261 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 4707 | 0x1263 | 2 | cmcIIIVarMax | 65535
InputRegister | ReadOnly | 2 | 4709 | 0x1265 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 4711 | 0x1267 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 4713 | 0x1269 | 2 | reserved
InputRegister | ReadOnly | 2 | 4715 | 0x126B | 2 | cmcIIIVarValueInt | Monitoring.Error List.Error 2 104
InputRegister | ReadOnly | 2 | 4717 | 0x126D | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4719 | 0x126F | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 4720 | 0x1270 | 32 | cmcIIIVarName | Monitoring.Error List.Error 2
InputRegister | ReadOnly | 2 | 4752 | 0x1290 | 3 | reserved
InputRegister | ReadOnly | 2 | 4755 | 0x1293 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 4763 | 0x129B | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 4765 | 0x129D | 2 | cmcIIIVarMax | 65535
InputRegister | ReadOnly | 2 | 4767 | 0x129F | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 4769 | 0x12A1 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 4771 | 0x12A3 | 2 | reserved
InputRegister | ReadOnly | 2 | 4773 | 0x12A5 | 2 | cmcIIIVarValueInt | Monitoring.Error List.Error 3 105
InputRegister | ReadOnly | 2 | 4775 | 0x12A7 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4777 | 0x12A9 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 4778 | 0x12AA | 32 | cmcIIIVarName | Monitoring.Error List.Error 3
InputRegister | ReadOnly | 2 | 4810 | 0x12CA | 3 | reserved
InputRegister | ReadOnly | 2 | 4813 | 0x12CD | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 4821 | 0x12D5 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 4823 | 0x12D7 | 2 | cmcIIIVarMax | 65535
InputRegister | ReadOnly | 2 | 4825 | 0x12D9 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 4827 | 0x12DB | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 4829 | 0x12DD | 2 | reserved
InputRegister | ReadOnly | 2 | 4831 | 0x12DF | 2 | cmcIIIVarValueInt | Monitoring.Error List.Error 4 106
InputRegister | ReadOnly | 2 | 4833 | 0x12E1 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4835 | 0x12E3 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 4836 | 0x12E4 | 32 | cmcIIIVarName | Monitoring.Error List.Error 4
InputRegister | ReadOnly | 2 | 4868 | 0x1304 | 3 | reserved
InputRegister | ReadOnly | 2 | 4871 | 0x1307 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 4879 | 0x130F | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 4881 | 0x1311 | 2 | cmcIIIVarMax | 65535
InputRegister | ReadOnly | 2 | 4883 | 0x1313 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 4885 | 0x1315 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 4887 | 0x1317 | 2 | reserved
InputRegister | ReadOnly | 2 | 4889 | 0x1319 | 2 | cmcIIIVarValueInt | Monitoring.Error List.Error 5 107
InputRegister | ReadOnly | 2 | 4891 | 0x131B | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4893 | 0x131D | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 4894 | 0x131E | 32 | cmcIIIVarName | Monitoring.Error List.Error 5
InputRegister | ReadOnly | 2 | 4926 | 0x133E | 3 | reserved
InputRegister | ReadOnly | 2 | 4929 | 0x1341 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 4937 | 0x1349 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 4939 | 0x134B | 2 | cmcIIIVarMax | 65535
InputRegister | ReadOnly | 2 | 4941 | 0x134D | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 4943 | 0x134F | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 4945 | 0x1351 | 2 | reserved
InputRegister | ReadOnly | 2 | 4947 | 0x1353 | 2 | cmcIIIVarValueInt | Monitoring.Error List.Error 6 108
InputRegister | ReadOnly | 2 | 4949 | 0x1355 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 4951 | 0x1357 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 4952 | 0x1358 | 32 | cmcIIIVarName | Monitoring.Error List.Error 6
InputRegister | ReadOnly | 2 | 4984 | 0x1378 | 3 | reserved
InputRegister | ReadOnly | 2 | 4987 | 0x137B | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 4995 | 0x1383 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 4997 | 0x1385 | 2 | cmcIIIVarMax | 65535
InputRegister | ReadOnly | 2 | 4999 | 0x1387 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 5001 | 0x1389 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 5003 | 0x138B | 2 | reserved
InputRegister | ReadOnly | 2 | 5005 | 0x138D | 2 | cmcIIIVarValueInt | Monitoring.Error List.Error 7 109
InputRegister | ReadOnly | 2 | 5007 | 0x138F | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 5009 | 0x1391 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 5010 | 0x1392 | 32 | cmcIIIVarName | Monitoring.Error List.Error 7
InputRegister | ReadOnly | 2 | 5042 | 0x13B2 | 3 | reserved
InputRegister | ReadOnly | 2 | 5045 | 0x13B5 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 5053 | 0x13BD | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 5055 | 0x13BF | 2 | cmcIIIVarMax | 65535
InputRegister | ReadOnly | 2 | 5057 | 0x13C1 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 5059 | 0x13C3 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 5061 | 0x13C5 | 2 | reserved
InputRegister | ReadOnly | 2 | 5063 | 0x13C7 | 2 | cmcIIIVarValueInt | Monitoring.Error List.Error 8 110
InputRegister | ReadOnly | 2 | 5065 | 0x13C9 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 5067 | 0x13CB | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 5068 | 0x13CC | 32 | cmcIIIVarName | Monitoring.Error List.Error 8
InputRegister | ReadOnly | 2 | 5100 | 0x13EC | 3 | reserved
InputRegister | ReadOnly | 2 | 5103 | 0x13EF | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 5111 | 0x13F7 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 5113 | 0x13F9 | 2 | cmcIIIVarMax | 65535
InputRegister | ReadOnly | 2 | 5115 | 0x13FB | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 5117 | 0x13FD | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 5119 | 0x13FF | 2 | reserved
InputRegister | ReadOnly | 2 | 5121 | 0x1401 | 2 | cmcIIIVarValueInt | Monitoring.Error List.Status 111
InputRegister | ReadOnly | 2 | 5123 | 0x1403 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 5125 | 0x1405 | 1 | cmcIIIVarType | 7
InputRegister | ReadOnly | 2 | 5126 | 0x1406 | 32 | cmcIIIVarName | Monitoring.Error List.Status
InputRegister | ReadOnly | 2 | 5158 | 0x1426 | 32 | cmcIIIVarConstraints | 1,4
InputRegister | ReadOnly | 2 | 5190 | 0x1446 | 2 | reserved
InputRegister | ReadOnly | 2 | 5192 | 0x1448 | 2 | cmcIIIVarValueInt | Monitoring.Error List.Category 112
InputRegister | ReadOnly | 2 | 5194 | 0x144A | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 5196 | 0x144C | 1 | cmcIIIVarType | 14
InputRegister | ReadOnly | 2 | 5197 | 0x144D | 32 | cmcIIIVarName | Monitoring.Error List.Category
InputRegister | ReadOnly | 2 | 5229 | 0x146D | 3 | reserved
InputRegister | ReadOnly | 2 | 5232 | 0x1470 | 8 | cmcIIIVarUnit
InputRegister | ReadOnly | 2 | 5240 | 0x1478 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 5242 | 0x147A | 2 | cmcIIIVarMax | 255
InputRegister | ReadOnly | 2 | 5244 | 0x147C | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 5246 | 0x147E | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 5248 | 0x1480 | 2 | reserved
InputRegister | ReadOnly | 2 | 5250 | 0x1482 | 2 | cmcIIIVarValueInt | Monitoring.Input Power 113
InputRegister | ReadOnly | 2 | 5252 | 0x1484 | 2 | cmcIIIVarLastChange
InputRegister | ReadOnly | 2 | 5254 | 0x1486 | 1 | cmcIIIVarType | 2
InputRegister | ReadOnly | 2 | 5255 | 0x1487 | 32 | cmcIIIVarName | Monitoring.Input Power
InputRegister | ReadOnly | 2 | 5287 | 0x14A7 | 3 | reserved
InputRegister | ReadOnly | 2 | 5290 | 0x14AA | 8 | cmcIIIVarUnit | W
InputRegister | ReadOnly | 2 | 5298 | 0x14B2 | 2 | cmcIIIVarMin | 0
InputRegister | ReadOnly | 2 | 5300 | 0x14B4 | 2 | cmcIIIVarMax | 10000
InputRegister | ReadOnly | 2 | 5302 | 0x14B6 | 2 | cmcIIIVarScale | 1
InputRegister | ReadOnly | 2 | 5304 | 0x14B8 | 2 | cmcIIIVarSteps | 1
InputRegister | ReadOnly | 2 | 5306 | 0x14BA | 2 | reserved
DeviceIdentification | ReadOnly | 2 | 0 | 0x00 | 10 | vendor name | Rittal GmbH & Co. KG
DeviceIdentification | ReadOnly | 2 | 1 | 0x01 | 2 | product code | CMC
DeviceIdentification | ReadOnly | 2 | 2 | 0x02 | 2 | major.minor version | 1.04
DeviceIdentification | ReadOnly | 2 | 3 | 0x03 | 11 | vendor URL | http://www.rittal.com
DeviceIdentification | ReadOnly | 2 | 4 | 0x04 | 32 | product name | CMCIII
DeviceIdentification | ReadOnly | 2 | 5 | 0x05 | 32 | model name | Computer Multi Control III
DeviceIdentification | ReadOnly | 2 | 6 | 0x06 | 4 | application name | cmc3mbd
DeviceIdentification | ReadOnly | 2 | 128 | 0x80 | 2 | mac address | n/a
DeviceIdentification | ReadOnly | 2 | 129 | 0x81 | 5 | cmcIIIDevSerial | 0x135177
DeviceIdentification | ReadOnly | 2 | 130 | 0x82 | 32 | cmcIIIDevName | Blue e+
DeviceIdentification | ReadOnly | 2 | 131 | 0x83 | 16 | cmcIIIDevArtNr | 3185830
DeviceIdentification | ReadOnly | 2 | 132 | 0x84 | 16 | cmcIIIDevFW | SW: 1.11.2 - FW: 2.6.0
DeviceIdentification | ReadOnly | 2 | 133 | 0x85 | 16 | cmcIIIDevHW | 1.0.0
DeviceIdentification | ReadOnly | 2 | 134 | 0x86 | 2 | cmcIIIUnitOSRev | n/a
DeviceIdentification | ReadOnly | 2 | 135 | 0x87 | 4 | cmcIIIDevProductWeek | 18/2018
DeviceIdentification | ReadOnly | 2 | 136 | 0x88 | 32 | cmcIIIDevAlias | Blue e Plus
DeviceIdentification | ReadOnly | 2 | 137 | 0x89 | 32 | cmcIIIDevLocation | Location
DeviceIdentification | ReadOnly | 2 | 138 | 0x8A | 64 | cmcIIIDevAssembly